## BOQ
BILL OF QUANTITY
Subject :-SITC of 6 x 2.0 TR and 3 x 2.25 TR modular ceiling/floor FCU and associated works at room 106-110 at JEE building.
Name of agency:-
S.No | Description | Qty | Unit | Rate | Amount
1 | SITC of modular type Fan Coil Unit (floor/wall-mounted) , The unit shall be complete with grills, insulated enclosure, drain tray, comprising of blower, 2/3 speed fan motor, 2/3 row copper coil section, washable filter section, 2 way motorised valve with actuator, and brass flair fitting for copper pipe connection, i/c all necessary support /hangers, vibration isolators etc. complete as reqd.
a) | 2.0 TR nominal or higher capacity | 6 | No. |  | 0
b) | 2.25 TR nominal or higher capacity | 3 | No. |  | 0
2 | Providing and fixing Digital controler (Thermostate) in fan coil units of up to 3.5 TR Capacity re-commissioning i/c dismantling old if any etc. complete as reqd. | 9 | No. |  | 0
3 | Cutting & Dismantling of condensor / chilled water pipe line of following size for drain out the water from supply & return pipe line and making good i/c re-filling of water in pipe line ,testing & commissioning complete as required. |  |  |  | 0
a) | Up to 200 mm dia | 2 | Job |  | 0
4 | Drain out the water from condensor / chilled supply & return pipe line and making good i/c re-filling of water in pipe line ,testing & commissioning complete as required. |  |  |  | 0
a) | Up to 200 mm dia | 4 | Job |  | 0
5 | Cutting & dismantling of damaged and defective insulation, removing the thermocole , nitrile, PUF insulation or clading from chilled water MS pipe line of size mentioned below including hessian cloth, wire mesh, sand, cement, plaster, cleaning of pipe and shifting the waste material within the permises of I.I.T. K. campus or desired location as reqd. |  |  |  | 0
a) | 20 mm to 80 mm dia. | 3 | Mtr |  | 0
6 | Supply, laying /fixing, testing and commissioning of MS Heavy 'C' class pipe ( IS :1239) of following sizes for chilled/ condenser water piping on surface / underground ( including fabrication of bends / elbows, tees, reducers, sockets, unions etc) with wooden / Puff block, masonry support / MS angle-clamp two coats primer/ enamel paint, vibration isolators and fittings as per standard specification complete as required. |  |  |  | 0
a) | 25 mm | 48 | Mtr |  | 0
b) | 32 mm | 42 | Mtr |  | 0
c) | 40 mm | 12 | Mtr |  | 0
7 | Supplying & fixing insulation on existing MS 'C' class pipe over exposed surface/underground of following sizes with 50 mm thick fire retardant thermocole ( polystyrene) moulded pipe section of density 20 kg/cu.m after a thick coat of cold setting adhesive (CPRX compound) , 500g polythene faced hessian cloth, wiremesh, sand-cement plaster & painting two or more coat to give even shade after applying one coat of ordinary paint etc complete as required. (Note:- Thermocole density should not be less than 20 kg/cu.m) |  |  |  | 0
a) | 25 mm | 48 | Mtr |  | 0
b) | 32 mm | 42 | Mtr |  | 0
c) | 40 mm | 12 | Mtr |  | 0
8 | Providing & fixing of thermal insulation with aluminium foil faced nitral rubber Class 'O' insulation sheet of following thickness on existing surface of pipe/duct with adhesive.The joints shall be sealed with 50 mm wide and self adhesive PVC/Aluminum tape complete as required. |  |  |  | 0
a) | 9 mm | 40 | SqM |  | 0
9 | Supply,fixing testing and commissioning of Stainless steel ball valve size as mentioned below ISI marked with socket and nipple for drain line as per standard specifications. |  |  |  | 0
a) | 25 mm | 4 | Nos |  | 0
10 | Providing & fixing of Brass ball valve of following size with compatible to proportioning Copper/MS pipe i/c all necessary accessories, support /hangers, including old dismantling if any complete as reqd. |  |  |  | 0
a) | 25 mm | 9 | Nos |  | 0
11 | Providing & fixing of Brass Ball valve with Y-strainer of following size with compatible to proportioning Copper/MS pipe i/c all necessary support /hangers & dismantling old if any complete as reqd. |  |  |  | 0
a) | 25 mm | 9 | Nos |  | 0
12 | SITC of Butterfly valves CI body with SS Disc Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water with hand lever operated including nut, bolt, flanges, gasket as kind of existing pipe, painting with enamel including dismantling etc. complete as reqd. |  |  |  | 0
a) | 40 mm | 4 | Nos |  | 0
13 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge. Internal work - Exposed on wall |  |  |  | 0
a) | 25 mm nominal outer dia pipes | 42 | Mtr |  | 0
b) | 32 mm nominal outer dia pipes | 26 | Mtr |  | 0
14 | Providing, laying, testing, and commissioning of following size Un-armoured PVC insulated Copper conducter power/controle cable of following size on surface/recessed complete as required. |  |  |  | 0
a) | 3 Core x 1.5 Sqmm, flexible Un-armoured copper cable | 30 | Mtr |  | 0
15 | Providing and fixing of 3 pin- 6 Amp. Single Phase Plug top ISI Marked for AC (FCU) unit complete as required. (Make:- Anchor or Equvilant) |  |  |  | 0
a) | 6 Amp | 9 | Nos |  | 0
16 | Supply and fixing UPVC mini trunking (casing-caping) & flexible conduit of following size white-system with independent cover- without central partion etc. as reqd |  |  |  | 0
a) | UPVC trunking 20mm x 12mm | 24 | Mtr |  | 0
b) | Flexi Conduit 20 mm | 12 | Mtr |  | 0
17 | Providing,laying & fixing of rainforced fiber flexible/soft PVC pipe of size given below etc. complete as reqd. |  |  |  | 0
a) | 20 mm | 2 | Mtr |  | 0
18 | Supply & fixing of copper piping 5/8" or 6/8" with 19 mm thick Class "O" Nitrile insulation on surface / recessed with flair nut, clamps etc. complete as reqd. | 18 | Mtr |  | 0
19 | Dismantling of Fan coil unit of Hi-wall/wall/floor mounted or ceiling suspended type up to 3.5 TR capacity including filter and valves etc. Complete as required. | 5 | Nos |  | 0
20 | Making wall opening upto 600mm dia in any type / thick of wall and re-closing the opening with brick, sand, cement and plaster upto 20 mm i/c re-painting as per existing desigine/shape complete as required. | 8 | Job |  | 0
21 | S/Replacement of defective and damaged aluminium clading with 26 swg thick aluminium sheet cladding, fixing with screws complete as required (Make-Hindalco/Equv). | 35 | SQM |  | 0
| Sub Total-A |  |  |  | 0
22 | Buy back cost of existing any type FCU(AC) following capacity with associated parts, controller etc and taken away from site Complete as required. |  |  |  | 0
a) | Upto 2.0 tr | 2 | Nos |  | 0
b) | Above 2.0 tr | 3 | Nos |  | 0
| Sub Total-B |  |  |  | 0
| Sub Total (A-B) |  |  |  | 0