## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Executive Engineer, IWD IIT Kanpur
Name of Work: Rejuvenation of old single skin AHU/LLD Blower of (Microfabrication lab) with double skin 8000 CFM AHU, VFD, VAV's and associated works at WL-130.
Contract No: 58/AC/2020/484 dt. 09.03.2020
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder in Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | Supply of double skin Horrizontal type Floor mounted air handling units (AHU) of panels consisting of pre coated G.I. casing of thickness 0.6 mm outside layer and 0.6 mm inside layer with 46/50 mm thick injected PUF of density not less than 40Kg/CuM .The air handling units shall be complete with mixing chamber box with manually Supply,Return & Fresh air aluminium damper, Filter-section with 50 mm thick boxs type synthetic fiber washable pre-filter's section EU-4 (90% down to 10 microns) & flange type bag filter section EU-4 (99% down to 3 microns), coil section with 6 Rows deep chilled water cooper coil & aluminium fins construction , fire retardent flexible connection, 20 G SS-304 stainless steel drain pan, fan section complete with forward/backward curved DIDW centrifugal fan , V-belts, drive package, VFD compatible variable speed squirrel cage induction motor, Motor shall be suitable for 415±10% volts, 50 Hz, 3 phase AC supply. and vibration isolator all complete as per standerd specifications. AHUs shall be selected for a maximum face velocity of 500 FPM (2.5 MPS), fan outlet velocity shall not exceed 1900 FPM (9.5m/s) | Item1 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | 8000 cfm, 6 Rows, static pressure 50 FM AHU with mixing chamber | item2 | 1 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | SITC of Pressure Independent Variable Air voulme(VAV) Terminal units, suitable for installtion in horizontal ducts. The casing shall be made of min. 0.8 mm GSS sheet internally accoustic lined with polymer foam/nitral insulation and . It shall include all accessories such as single / multileaf damper (with equal % characteristics), Diff. pressure transmitter actuators, aero cross sensor, transformer (220v/24v), cntroller box,hangers i/c digital thermostat with LCD display (Honeywell/Neptronics/Belimo or equiv.), and factory tested/calibrated values of V-min, V-max, V-nom, feed back control cabling and any other ancilary requirement for the functioning of the units. The VAV shall be modbus/ Bacnet supported. | item3 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2.01 | Min 80cfm-Max 800cfm | item4 | 3 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
3 | SITC of variable frequency drive (VFD) of model no.FC-102/ Equvilant, with IP20, H2 RFI filter,Lcp of make Danfoss/equivalent & Resistive Tempearature Device (RTD) Make- Omricon/equvilant along with necessary Control/communication wiring in flexible condute for maximum energy conservation with following specifications complete as required. | item5 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
3.01 | 4.0 Kw | Item6 | 1 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4 | Dismantling & removing of damaged and defective thermal insulation of any thickness i.e. nitrile, , polystyrene foam, paramount, PVC tape etc. from existing duct/planum and shifting the waste material within the premises of I.I.T. K. campus or desired location as reqd. | Item7 | 30 | sqmtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
5 | Dismantling and removing of existing old ducts of any size, i/c removing of hangers, flanges,demper, diffuser, grill etc and depositing in the sectional store complete as reqd. | Item8 | 50 | sqmtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
6 | Cutting & dismantling of damaged and defective insulation, removing the thermocole , Nitrile, PUF insulation or cladding from chilled water MS pipe line of size mentioned below including hessian cloth, wire mesh, sand, cement, plaster, cleaning of pipe and shifting the waste material within the premises of I.I.T. K. campus or desired location. | Item9 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
6.01 | 20 mm to 100 mm dia. | Item10 | 6 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7 | Cutting & Dismantling of condensor / chilled water pipe line of following size for drain out the water from supply & return pipe line and making good i/c re-filling of water in pipe line ,testing & commissioning complete as required. | Item11 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7.01 | 25 mm to 200 mm dia | Item12 | 1 | Job | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
8 | Dismantling & removing of Air handling unit / LLD Blower with associated parts, valve, damper etc and disconnecting from CHW line & ducting complete as reqd. | Item13 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
8.01 | Up to 12000 CFM | Item14 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
9 | Buy back cost of existing Air handling unit / LLD Blower with associated parts and taken away from site Complete as required (excluding motors and cable etc). | Item15 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9.01 | Up to 12000 CFM | Item16 | 1 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
10 | Supply, installation, balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. | Item17 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
10.01 | 0.63 mm (24 G) thick | Item18 | 75 | SqM | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
10.02 | 0.80 mm (22 G) thick | Item19 | 70 | SqM | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
11 | Providing & fixing of acoustic insulation with open cell Nitrile rubber sheet(Accosound) super silence of following thickness, on existing surface with adhesive and accessories etc. complete as required. | Item20 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
11.01 | 10 mm | Item21 | 50 | Sqm | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
12 | Supply and fixing of acoustic lining of supply air duct and plenum with 25 mm thick resin bonded glass wool having density of 32 kg/m³, with 25 mm X 25 mm GI section of 1.25 mm thick, at 600 mm centre to centre covered with Reinforced Plastic tissue paper and 0.5 mm thick perforated aluminium sheet fixed to inside surface of ducts with cadmium plated nuts, bolts, stick pins, CPRX compound etc. complete as required and as per specifications. | Item22 | 55 | SqM | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
13 | Providing & fixing of thermal insulation with aluminium foil faced XLPE Class 'O' insulation sheet of following thickness on existing surface of duct with dendrite/adhesive and tightning with packing strip & lock at approx every 1.0 mtr distance etc.The joints shall be sealed with 50 mm wide and self adhesive PVC/Aluminium tape complete as required. | Item23 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
13.01 | 13 mm | Item24 | 125 | SqM | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14 | Providing & fixing of thermal insulation without aluminium foil faced XLPE Class 'O' insulation sheet of following thickness on existing surface of duct with dendrite/adhesive and tightning with packing strip & lock at approx every 1.0 mtr distance etc.The joints shall be sealed with 50 mm wide and self adhesive PVC/Aluminium tape complete as required. | Item25 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
14.01 | 13 mm | Item26 | 125 | SqM | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
15 | Supplying & fixing of powder coated extruded aluminium Supply Air Grills with aluminium volume control dampers as per specifications | Item27 | 3 | SqM | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
16 | Supplying & fixing of powder coated extruded aluminium Return Air Grills with lowers but without aluminium volume control dampers as reqd | Item28 | 4 | SqM | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
17 | Supply, installation, testing and commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc, as per specifications. | Item29 | 2 | SqM | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
18 | Supply, laying /fixing, testing and commissioning of MS Heavy 'C' class pipe ( IS :1239) of following sizes for chilled/ condenser water piping on surface / underground ( including fabrication of bends / elbows, tees, reducers, sockets, unions etc) with wooden / Puff block, masonry support / MS angle-clamp two coats primer/ enamel paint, vibration isolators and fittings as per standard specification complete as required. | Item30 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
18.01 | 65 mm | Item31 | 9 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
18.02 | 50 mm | Item32 | 8 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
18.03 | 40 mm | Item33 | 2 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19 | Supplying & fixing insulation on existing MS 'C' class pipe over exposed surface/underground of following sizes with 50 mm thick fire retardant thermocole ( polystyrene) moulded pipe section of density 20 kg/cu.m after a thick coat of cold setting adhesive (CPRX compound) , 500g polythene faced hessian cloth, wiremesh, sand-cement plaster & painting two or more coat to give even shade after applying one coat of ordinary paint etc complete as required. (Note:- Thermocole density should not be less than 20 kg/cu.m) | Item34 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
19.01 | 65 mm | Item35 | 9 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
19.02 | 50 mm | Item36 | 8 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
19.03 | 40 mm | Item37 | 2 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20 | Supplying, fixing, testing and commissioning of following Y - STRAINER of Ductile CI Body flanged ends with stainless steel strainer for chilled / hot water circulation including insulation as specified. | Item38 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
20.01 | 65 mm | Item39 | 1 | Nos | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
21 | Supplying and fixing testing and commissioning of stainless steel ball valve size as mentioned below ISI marked with socket and nipple for drain line as per standard specifications. | Item40 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
21.01 | 20 mm | Item41 | 1 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
21.02 | 25 mm | Item42 | 1 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
22 | SITC of Butterfly valves CI body with SS Disc Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water with hand lever operated including nut, bolt, flanges, gasket as kind of existing pipe, painting with enamel including dismantling etc. complete as reqd. | Item43 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
22.01 | 65 mm | Item44 | 2 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
22.02 | 50 mm | Item45 | 1 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
23 | Supply & fixing of fire retardant double cloth canvass made (up to 300 mm vide) with heavy clothes and suitable frame with G.I washer, nuts & bolts in suitable size. i/c jointing both sides with suitable gaskets complete as reqd. | Item46 | 3 | Job | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
24 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes, having thermal stability for hot & cold water supply, including all CPVC plain & brass threaded fittings, including fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and testing of joints complete as per direction of Engineer in Charge. Internal work - Exposed on wall | Item47 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
24.01 | 32 mm nominal outer dia pipes | Item48 | 10 | Mtr | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
25 | P & F DLP trunking of following size white-system with independent cover- without central partion & with End cap, Flat angle etc as reqd (Make- Legrand/Equiv). | Item49 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
25.01 | DLP 105*50 mm | Item50 | 0.6 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
25.02 | Flexi Cover 85 mm | Item51 | 0.6 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
25.03 | End cap | Item52 | 6 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
26 | Providing, laying, testing, and commissioning of following size Un-armoured PVC insulated Copper conducter power/controle cable of following size on surface/recessed complete as required. | Item53 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
26.01 | 3 Core x 1.5 Sqmm, flexible Un-armoured copper cable | Item54 | 15 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
26.02 | 4 Core x 6.0 Sqmm, flexible Un-armoured copper cable | Item55 | 12 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
27 | Providing and fixing 6 SWG dia G.l. wire on surface or in recess for loop earthling as required | Item56 | 12 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
28 | Supplying and fixing of following sizes of medium class PVC conduit along with accessories in surface/recess including cutting the wall and making good the same in case of recessed conduit as required. | Item57 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
28.01 | 20 mm | Item58 | 12 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
29 | Providing and fixing of 3 pin- 6 Amp. Single Phase Plug top ISI Marked for AC (VAV) unit complete as required. (Make:- Anchor or Equvilant) | Item59 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
29.01 | 6 Amp | Item60 | 3 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
30 | Supply and fixing UPVC mini trunking (casing-caping) & flexible conduit of following size white-system with independent cover- without central partion etc. as reqd | Item61 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
30.01 | UPVC trunking 20mm x 12mm | Item62 | 10 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
30.02 | Flexi Conduit 20 mm | Item63 | 10 | Mtr | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
31 | P & F ,testing and commissioning of 32 Amp. Three Phase MCB with 2/4 Way powder coated MS Box enclosure suitable for Motor upto 5.5 Kw complete as required. | Item64 | 1 | Nos | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
32 | Demolishing brick work i/c stacking of serviceable mat. with in 50 mtrs lead. In cement mortar | Item65 | 3 | CuM | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | INR Zero Only | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | Zero Only
Quoted Rate in Words |  | INR Zero Only

## Macros
Please Enable Macros to View BoQ information