## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.1 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: DOIP, IIT Kanpur
Name of Work: SITC of VRF Air-conditioning system in Core lab building, Lab 104, IIT Kanpur.
NIT No: EandM/02/06/2023-1
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | Component | [53 empty] | 1 | Component
1.01 | OUTDOOR UNIT | item no.1 | [52 empty] | 1.01 | OUTDOOR UNIT | item no.1 |  |  | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.02 | Supply Installation, Testing & Commissioning of modular type Variable Refrigerant Flow/Variable Refrigerant Volume air cooled Outdoor units suitable for cooling and heating, having all hermetically sealed inverter type Scroll Compressor(s), minimum two compressors for above 16 HP modules, microprocessor based Controller, top discharge type condensing unit(s), with R 410 A Refrigerant, vibration isolators, with suitable foundation etc. complete as required. The unit shall deliver the rated capacity at AHRI Conditions and work even at 50°C ambient temperature without tripping. The unit shall be suitable to work on 400V +/- 10%, 3 Phase, 50Hz AC power supply. The unit shall be filled with first charge of the refrigerant and ready for use as required. The COP at AHRI conditions shall not be less than 3.1 and IEER not less than 6.5. | item no.2 | [52 empty] | 1.02 | Supply Installation, Testing & Commissioning of modular type Variable Refrigerant Flow/Variable Refrigerant Volume air cooled Outdoor units suitable for cooling and heating, having all hermetically sealed inverter type Scroll Compressor(s), minimum two compressors for above 16 HP modules, microprocessor based Controller, top discharge type condensing unit(s), with R 410 A Refrigerant, vibration isolators, with suitable foundation etc. complete as required. The unit shall deliver the rated capacity at AHRI Conditions and work even at 50°C ambient temperature without tripping. The unit shall be suitable to work on 400V +/- 10%, 3 Phase, 50Hz AC power supply. The unit shall be filled with first charge of the refrigerant and ready for use as required. The COP at AHRI conditions shall not be less than 3.1 and IEER not less than 6.5. | item no.2 |  |  | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.03 | 20 HP capacity of Outdoor Unit | item no.3 | 20 | HP | 21081 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 421620 | 421620 | INR Four Lakh Twenty One Thousand Six Hundred & Twenty Only | 1.03 | 20 HP capacity of Outdoor Unit | item no.3 | 20 | HP | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.04 | Supply, installation, testing and commissioning of following capacity unit high static pressure VRF/VRV ceiling mounted ductable type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, corded remote control, outer cabinet, vibration isolators, drain pan, other necessary supports etc., suitable for operation on single phase AC supply 230 V ± 10%, 50 Hz complete as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. | item no.4 | [52 empty] | 1.04 | Supply, installation, testing and commissioning of following capacity unit high static pressure VRF/VRV ceiling mounted ductable type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, corded remote control, outer cabinet, vibration isolators, drain pan, other necessary supports etc., suitable for operation on single phase AC supply 230 V ± 10%, 50 Hz complete as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. | item no.4
1.05 | Min. Capacity 8.0 Tr /2550 CFM, 22 mm WG S.P | item no.5 | 2 | Nos | 107349 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 214698 | 214698 | INR Two Lakh Fourteen Thousand Six Hundred & Ninety Eight Only | 1.05 | Min. Capacity 8.0 Tr /2550 CFM, 22 mm WG S.P | item no.5 | 2 | Nos
1.06 | Supply Installation, Testing and commissioning of Imported fittings (Ref Net) Y-joints etc. | item no.6 | [52 empty] | 1.06 | Supply Installation, Testing and commissioning of Imported fittings (Ref Net) Y-joints etc. | item no.6
1.07 | Y joints for IDU | item no.7 | 1 | Nos. | 5600 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5600 | 5600 | INR Five Thousand Six Hundred Only | 1.07 | Y joints for IDU | item no.7 | 1 | Nos.
1.08 | SITC Cordless/ Corded Remotes controllers for indoor units having function of temp. control, different operating modes, timer etc. | item no.8 | 2 | Nos | 3834 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7668 | 7668 | INR Seven Thousand Six Hundred & Sixty Eight Only | 1.08 | SITC Cordless/ Corded Remotes controllers for indoor units having function of temp. control, different operating modes, timer etc. | item no.8 | 2 | Nos | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.09 | COPPER REFRIGERANT PIPING | item no.9 | [52 empty] | 1.09 | COPPER REFRIGERANT PIPING | item no.9 |  |  | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.1 | Supply, Installation, testing and commissioning including vaccumiazation and Nitrogen testing of following nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XPLE Class-O tubular insulation/with Class-O closed cell elastomeric nitrile rubber tubular sleeves sections of specified thickness as given below for Suction and Liquid lines, all accessories as per specifications etc. as required : | item no.10 | [52 empty] | 1.1 | Supply, Installation, testing and commissioning including vaccumiazation and Nitrogen testing of following nominal sizes of soft/hard drawn copper refrigerant piping for VRV/VRF system, complete with fittings, with suitable adjustable ring type hanger supports, jointing/brazing including accessories, insulated with XPLE Class-O tubular insulation/with Class-O closed cell elastomeric nitrile rubber tubular sleeves sections of specified thickness as given below for Suction and Liquid lines, all accessories as per specifications etc. as required : | item no.10 |  |  | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.11 | 9.5 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 19mm thick insulation | item no.11 | 30 | Mtr | 350 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 10500 | 10500 | INR Ten Thousand Five Hundred Only | 1.11 | 9.5 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 19mm thick insulation | item no.11 | 30 | Mtr
1.12 | 22.2 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19 mm thick insulation | item no.12 | 30 | Mtr | 960 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 28800 | 28800 | INR Twenty Eight Thousand Eight Hundred Only | 1.12 | 22.2 mm dia (OD) (Hard drawn) with tube thickness 1.2 mm with 19 mm thick insulation | item no.12 | 30 | Mtr
1.13 | 15.86 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 19 mm thick insulation | item no.13 | 15 | Mtr | 450 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 6750 | 6750 | INR Six Thousand Seven Hundred & Fifty Only | 1.13 | 15.86 mm dia (OD) (Soft drawn) with tube thickness 1.2 mm with 19 mm thick insulation | item no.13 | 15 | Mtr
1.14 | 34.9 mm dia (OD) (Hard drawn) with tube thickness 1.62 mm with 19 mm thick insulation | item no.14 | 15 | Mtr | 1645 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 24675 | 24675 | INR Twenty Four Thousand Six Hundred & Seventy Five Only | 1.14 | 34.9 mm dia (OD) (Hard drawn) with tube thickness 1.62 mm with 19 mm thick insulation | item no.14 | 15 | Mtr
1.15 | Supply, Installation, testing and commissioning of uPVC plumbing drain piping complete with, 9/6 mm Insulation, fittings, supports accessories in surface/recess as per specifications & site requirements | item no.15 | [52 empty] | 1.15 | Supply, Installation, testing and commissioning of uPVC plumbing drain piping complete with, 9/6 mm Insulation, fittings, supports accessories in surface/recess as per specifications & site requirements | item no.15
1.16 | 32 mm dia | item no.16 | 15 | Mtr | 199 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2985 | 2985 | INR Two Thousand Nine Hundred & Eighty Five Only | 1.16 | 32 mm dia | item no.16 | 15 | Mtr
1.17 | 25 mm dia | item no.17 | 20 | Mtr | 157 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3140 | 3140 | INR Three Thousand One Hundred & Forty Only | 1.17 | 25 mm dia | item no.17 | 20 | Mtr
1.18 | Duct Flexible Connectors: | item no.18 | [52 empty] | 1.18 | Duct Flexible Connectors: | item no.18
1.19 | SITC of Duct Flexible Connectors made out of Silicon Coated Non Combustible Fabric (Finished Width of 150 mm) suitable to withstand temperature of 280 Deg. C for 1 Hour, complete with fittings, flanges, supports, all accessories as per specifications and any other item required to make the system complete. | item no.19 | 2 | Sqmt | 2343 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4686 | 4686 | INR Four Thousand Six Hundred & Eighty Six Only | 1.19 | SITC of Duct Flexible Connectors made out of Silicon Coated Non Combustible Fabric (Finished Width of 150 mm) suitable to withstand temperature of 280 Deg. C for 1 Hour, complete with fittings, flanges, supports, all accessories as per specifications and any other item required to make the system complete. | item no.19 | 2 | Sqmt
1.2 | DUCTING | item no.20 | [52 empty] | 1.2 | DUCTING | item no.20
1.21 | Supply, installation, balancing and commissioning of Site Fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. | item no.21 | [52 empty] | 1.21 | Supply, installation, balancing and commissioning of Site Fabricated GSS sheet metal rectangular ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers, supports etc. as per approved drawings and specifications of following sheet thickness complete as required. | item no.21
1.22 | Thickness 0.63 mm sheet | item no.22 | 40 | Sqmt | 944.64 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 37785.6 | 37785.6 | INR Thirty Seven Thousand Seven Hundred & Eighty Five and Paise Sixty Only | 1.22 | Thickness 0.63 mm sheet | item no.22 | 40 | Sqmt
1.23 | Thickness 0.8 mm sheet | item no.23 | 30 | Sqmt | 1070 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 32100 | 32100 | INR Thirty Two Thousand One Hundred Only | 1.23 | Thickness 0.8 mm sheet | item no.23 | 30 | Sqmt
1.24 | Supply, installation, testing and commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc, as per specifications. | item no.24 | 1.5 | Sqmt | 6291.07 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 9436.61 | 9436.61 | INR Nine Thousand Four Hundred & Thirty Six and Paise Sixty One Only | 1.24 | Supply, installation, testing and commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc, as per specifications. | item no.24 | 1.5 | Sqmt
1.25 | Supplying & fixing of powder coated extruded aluminium supply Air Grills with Al. collar damper complete as required. | item no.25 | 2 | Sqmt | 8129.46 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 16258.92 | 16258.92 | INR Sixteen Thousand Two Hundred & Fifty Eight and Paise Ninety Two Only | 1.25 | Supplying & fixing of powder coated extruded aluminium supply Air Grills with Al. collar damper complete as required. | item no.25 | 2 | Sqmt
1.26 | Insulation Works: | item no.26 | [52 empty] | 1.26 | Insulation Works: | item no.26
1.27 | Supplying and fixing of acoustic lining of duct with Open Cell Nitrile Rubber density 140-180 Kg/m³. Applied by Adhesive, conforming to standard specification. | item no.27 | [52 empty] | 1.27 | Supplying and fixing of acoustic lining of duct with Open Cell Nitrile Rubber density 140-180 Kg/m³. Applied by Adhesive, conforming to standard specification. | item no.27
1.28 | 15 mm thick open cell nitrile rubber. | item no.28 | 20 | Sqmt | 1544 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 30880 | 30880 | INR Thirty Thousand Eight Hundred & Eighty Only | 1.28 | 15 mm thick open cell nitrile rubber. | item no.28 | 20 | Sqmt
1.29 | Supplying and fixing of following thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber (Class "O") insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required. | item no.29 | [52 empty] | 1.29 | Supplying and fixing of following thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber (Class "O") insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required. | item no.29
1.3 | 19 mm Thick | item no.30 | 70 | Sqmt | 851 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 59570 | 59570 | INR Fifty Nine Thousand Five Hundred & Seventy Only | 1.3 | 19 mm Thick | item no.30 | 70 | Sqmt
1.31 | Electrical Work | item no.31 | [52 empty] | 1.31 | Electrical Work | item no.31
1.32 | POWER CABLES | item no.32 | [52 empty] | 1.32 | POWER CABLES | item no.32
1.33 | Supply and laying of the following 1100 volts grade armoured XLPE insulated and PVC heated Copper conductor cable in existing trench / cable tray /clamped to wall with suitable clamps saddles & fixing bolts/including testing & commissioning complete as required. The costs shall include crimping tinned heavy duty copper lugs, compression glands requisite materials for all cables and to provide with 1D gap & shall be properly clamped with cable clamps & ties. Identification tags shall be provided for all cables including cable end termination. | item no.33 | [52 empty] | 1.33 | Supply and laying of the following 1100 volts grade armoured XLPE insulated and PVC heated Copper conductor cable in existing trench / cable tray /clamped to wall with suitable clamps saddles & fixing bolts/including testing & commissioning complete as required. The costs shall include crimping tinned heavy duty copper lugs, compression glands requisite materials for all cables and to provide with 1D gap & shall be properly clamped with cable clamps & ties. Identification tags shall be provided for all cables including cable end termination. | item no.33
1.34 | 5 core 16 Sq mm for ODU | item no.34 | 10 | Mtr | 1660 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 16600 | 16600 | INR Sixteen Thousand Six Hundred Only | 1.34 | 5 core 16 Sq mm for ODU | item no.34 | 10 | Mtr
1.35 | Supply and laying 6 SWG GI Earthing | item no.35 | 72 | Mtr | 46 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3312 | 3312 | INR Three Thousand Three Hundred & Twelve Only | 1.35 | Supply and laying 6 SWG GI Earthing | item no.35 | 72 | Mtr
1.36 | CONTROL CABLING | item no.36 | [52 empty] | 1.36 | CONTROL CABLING | item no.36
1.37 | Supply, laying, testing and commissioning of PVC insulated and PVC sheathed, shielded, Copper Conductor of 1.1 KV grade in PVC conduit, as per Standard specification including end termination as required. | item no.37 | [52 empty] | 1.37 | Supply, laying, testing and commissioning of PVC insulated and PVC sheathed, shielded, Copper Conductor of 1.1 KV grade in PVC conduit, as per Standard specification including end termination as required. | item no.37
1.38 | 2C x 1.5 Sq mm | item no.38 | 75 | Mtr | 252 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 18900 | 18900 | INR Eighteen Thousand Nine Hundred Only | 1.38 | 2C x 1.5 Sq mm | item no.38 | 75 | Mtr
1.39 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as req. | item no.39 | [52 empty] | 1.39 | Supplying and installing following size of perforated painted with powder coating M.S. cable trays with perforation not more than 17.5%, in convenient sections, joined with connectors, suspended from the ceiling with M.S. suspenders including bolts & nuts, painting suspenders etc as req. | item no.39
1.4 | 300 mm width X 50 mm depth X 1.6 mm thickness | item no.40 | 15 | Mtr | 693.75 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 10406.25 | 10406.25 | INR Ten Thousand Four Hundred & Six and Paise Twenty Five Only | 1.4 | 300 mm width X 50 mm depth X 1.6 mm thickness | item no.40 | 15 | Mtr
1.41 | SECTION - 'B' | item no.41 | [52 empty] | 1.41 | SECTION - 'B' | item no.41
1.42 | ANNUAL COMPREHENSIVE MAINTENANCE OF THE INSTALLED VRF SYSTEM FOR 01 YEARS | item no.42 | [52 empty] | 1.42 | ANNUAL COMPREHENSIVE MAINTENANCE OF THE INSTALLED VRF SYSTEM FOR 01 YEARS | item no.42
1.43 | Annual Comprehensive Maintenance Contract for period for 01 years (after 1 year of DLP). The contract shall include all spares, cosumables & replacement of defective/damaged parts as required to run the completely installed VRF system i.e outdoor unit, indoor unit etc complete as reqd. of capacity 20 HP through OEM. | item no.43 | [52 empty] | 1.43 | Annual Comprehensive Maintenance Contract for period for 01 years (after 1 year of DLP). The contract shall include all spares, cosumables & replacement of defective/damaged parts as required to run the completely installed VRF system i.e outdoor unit, indoor unit etc complete as reqd. of capacity 20 HP through OEM. | item no.43
1.44 | For 1st year (0-12 Months) | item no.44 | 12 | month | 3330 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 39960 | 39960 | INR Thirty Nine Thousand Nine Hundred & Sixty Only | 1.44 | For 1st year (0-12 Months) | item no.44 | 12 | month
Total in Figures | [51 empty] | 1006331.38 | 1006331.38 | Ten Lakh Six Thousand Three Hundred & Thirty One and Paise Thirty Eight Only
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | INR Zero Only
Quoted Rate in Words |  | INR Zero Only
Note on K18: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K21: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K16: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K20: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K24: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K25: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K26: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K27: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K29: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K30: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K32: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K35: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K36: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K37: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K38: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K41: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K43: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K47: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K48: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K51: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K53: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K57: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.

## Macros
Please Enable Macros to View BoQ information