## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.1 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: DOIP, IIT Kanpur
Name of Work: Renovation work in WL-215 at IIT Kanpur (SH: Civil & Electrical works)
NIT No: Composite/25/01/2024-1
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | CEMENT CONCRETE (CAST IN SITU) | item no.1 | [52 empty] | 1 | CEMENT CONCRETE (CAST IN SITU) | item no.1
2 | Providing and laying cement concrete in retaining walls, return walls, walls (any thickness) including attached pilasters, columns, piers, abutments, pillars, posts, struts, buttresses, string or lacing courses, parapets, coping, bed blocks, anchor blocks, plain window sills, fillets, sunken floor etc., up to floor five level, excluding the cost of centering, shuttering and finishing: | item no.2 | [52 empty] | 2 | Providing and laying cement concrete in retaining walls, return walls, walls (any thickness) including attached pilasters, columns, piers, abutments, pillars, posts, struts, buttresses, string or lacing courses, parapets, coping, bed blocks, anchor blocks, plain window sills, fillets, sunken floor etc., up to floor five level, excluding the cost of centering, shuttering and finishing: | item no.2
3 | 1:1½:3 (1 cement : 1½ coarse sand (zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources). |  | 0.15 | cum | 8587.24 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1288 | 1288 | INR One Thousand Two Hundred & Eighty Eight Only | 3 | 1:1½:3 (1 cement : 1½ coarse sand (zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources). |  | 0.15 | cum
4 | REINFORCED CEMENT CONCRETE | [53 empty] | 4 | REINFORCED CEMENT CONCRETE
5 | Reinforced cement concrete work in beams, suspended floors, roofs having slope up to 15° landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases above plinth level up to floor five level, excluding the cost of centering, shuttering, finishing and reinforcement with 1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources). |  | 0.92 | cum | 9398.77 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8647 | 8647 | INR Eight Thousand Six Hundred & Forty Seven Only | 5 | Reinforced cement concrete work in beams, suspended floors, roofs having slope up to 15° landings, balconies, shelves, chajjas, lintels, bands, plain window sills, staircases and spiral stair cases above plinth level up to floor five level, excluding the cost of centering, shuttering, finishing and reinforcement with 1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources). |  | 0.92 | cum
6 | Centering and shuttering including strutting, propping etc. and removal of form for | [53 empty] | 6 | Centering and shuttering including strutting, propping etc. and removal of form for
7 | Shelves (Cast in situ) |  | 14 | sqm | 672.12 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 9410 | 9410 | INR Nine Thousand Four Hundred & Ten Only | 7 | Shelves (Cast in situ) |  | 14 | sqm
8 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete above plinth level. | [53 empty] | 8 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete above plinth level.
9 | Thermo-Mechanically Treated bars of grade Fe-500D or more. |  | 108 | kg | 78.61 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8490 | 8490 | INR Eight Thousand Four Hundred & Ninety Only | 9 | Thermo-Mechanically Treated bars of grade Fe-500D or more. |  | 108 | kg
10 | MASONRY WORK | [53 empty] | 10 | MASONRY WORK
11 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in : | [53 empty] | 11 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in :
12 | Cement mortar 1:6 (1 cement : 6 coarse sand) |  | 1.5 | cum | 7267.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 10901 | 10901 | INR Ten Thousand Nine Hundred & One Only | 12 | Cement mortar 1:6 (1 cement : 6 coarse sand) |  | 1.5 | cum
13 | Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level. | [53 empty] | 13 | Half brick masonry with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level.
14 | Cement mortar 1:4 (1 cement :4 coarse sand) |  | 1.13 | sqm | 892.63 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1009 | 1009 | INR One Thousand &Nine Only | 14 | Cement mortar 1:4 (1 cement :4 coarse sand) |  | 1.13 | sqm
15 | CLADDING WORK | [53 empty] | 15 | CLADDING WORK
16 | Providing and fixing 18 mm thick gang saw cut, mirror polished, premoulded and prepolished, machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size, approved shade, colour and texture laid over 20 mm thick base cement mortar 1:4 (1 cement : 4 coarse sand), joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels. | [53 empty] | 16 | Providing and fixing 18 mm thick gang saw cut, mirror polished, premoulded and prepolished, machine cut for kitchen platforms, vanity counters, window sills, facias and similar locations of required size, approved shade, colour and texture laid over 20 mm thick base cement mortar 1:4 (1 cement : 4 coarse sand), joints treated with white cement, mixed with matching pigment, epoxy touch ups, including rubbing, curing, moulding and polishing to edges to give high gloss finish etc. complete at all levels.
17 | Granite stone slab colour black, Cherry/Ruby red | [53 empty] | 17 | Granite stone slab colour black, Cherry/Ruby red
18 | Area of slab over 0.50 sqm |  | 5.5 | sqm | 3880.18 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 21341 | 21341 | INR Twenty One Thousand Three Hundred & Forty One Only | 18 | Area of slab over 0.50 sqm |  | 5.5 | sqm
19 | Extra for providing opening of required size & shape for wash basin/ kitchen sink in kitchen platform, vanity counter and similar location in marble/ Granite/ stone work, including necessary holes for pillar taps etc. including moulding, rubbing and polishing of cut edges etc. complete. |  | 1 | each | 708.59 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 709 | 709 | INR Seven Hundred & Nine Only | 19 | Extra for providing opening of required size & shape for wash basin/ kitchen sink in kitchen platform, vanity counter and similar location in marble/ Granite/ stone work, including necessary holes for pillar taps etc. including moulding, rubbing and polishing of cut edges etc. complete. |  | 1 | each
20 | Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 (thickness to be specified by the manufacturer), of approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. |  | 8 | sqm | 932.44 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7460 | 7460 | INR Seven Thousand Four Hundred & Sixty Only | 20 | Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS: 15622 (thickness to be specified by the manufacturer), of approved make, in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge, in skirting, risers of steps and dados, over 12 mm thick bed of cement mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm, including pointing in white cement mixed with pigment of matching shade complete. |  | 8 | sqm
21 | WOOD AND P. V. C. WORK | [53 empty] | 21 | WOOD AND P. V. C. WORK
22 | Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters: | [53 empty] | 22 | Providing and fixing ISI marked flush door shutters conforming to IS : 2202 (Part I) non-decorative type, core of block board construction with frame of 1st class hard wood and well matched commercial 3 ply veneering with vertical grains or cross bands and face veneers on both faces of shutters:
23 | 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws |  | 3.87 | sqm | 1767.43 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 6840 | 6840 | INR Six Thousand Eight Hundred & Forty Only | 23 | 35 mm thick including ISI marked Stainless Steel butt hinges with necessary screws |  | 3.87 | sqm
24 | Extra for cutting rebate in flush door shutters (Total area of the shutter to be measured). |  | 3.87 | sqm | 82.11 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 318 | 318 | INR Three Hundred & Eighteen Only | 24 | Extra for cutting rebate in flush door shutters (Total area of the shutter to be measured). |  | 3.87 | sqm
25 | Providing and fixing ISI marked oxidised M.S. handles conforming to IS:4992 with necessary screws etc. complete : | [53 empty] | 25 | Providing and fixing ISI marked oxidised M.S. handles conforming to IS:4992 with necessary screws etc. complete :
26 | 100 mm |  | 2 | each | 24.77 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 50 | 50 | INR Fifty Only | 26 | 100 mm |  | 2 | each
27 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. complete. | [53 empty] | 27 | Providing and fixing oxidised M.S. casement stays (straight peg type) with necessary screws etc. complete.
28 | 250 mm weighing not less than 150 grams |  | 2 | each | 45.51 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 91 | 91 | INR Ninety One Only | 28 | 250 mm weighing not less than 150 grams |  | 2 | each
29 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm), with necessary accessories and screws etc. complete. |  | 1 | each | 899.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 899 | 899 | INR Eight Hundred & Ninety Nine Only | 29 | Providing and fixing aluminium die cast body tubular type universal hydraulic door closer (having brand logo with ISI, IS : 3564, embossed on the body, door weight upto 35 kg and door width upto 700 mm), with necessary accessories and screws etc. complete. |  | 1 | each
30 | Providing and fixing aluminium sliding door bolts, ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868), transparent or dyed to required colour or shade, with nuts and screws etc. complete : | [53 empty] | 30 | Providing and fixing aluminium sliding door bolts, ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868), transparent or dyed to required colour or shade, with nuts and screws etc. complete :
31 | 300x16 mm |  | 1 | each | 228.23 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 228 | 228 | INR Two Hundred & Twenty Eight Only | 31 | 300x16 mm |  | 1 | each
32 | Providing and fixing aluminium tower bolts, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868 ) transparent or dyed to required colour or shade, with necessary screws etc. complete : | [53 empty] | 32 | Providing and fixing aluminium tower bolts, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868 ) transparent or dyed to required colour or shade, with necessary screws etc. complete :
33 | 250x10 mm |  | 2 | each | 91.54 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 183 | 183 | INR One Hundred & Eighty Three Only | 33 | 250x10 mm |  | 2 | each
34 | Providing and fixing aluminium handles, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade, with necessary screws etc. complete : | [53 empty] | 34 | Providing and fixing aluminium handles, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade, with necessary screws etc. complete :
35 | 125 mm |  | 4 | each | 52.65 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 211 | 211 | INR Two Hundred & Eleven Only | 35 | 125 mm |  | 4 | each
36 | Providing and fixing aluminium hanging floor door stopper, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade, with necessary screws etc. complete. | [53 empty] | 36 | Providing and fixing aluminium hanging floor door stopper, ISI marked, anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour and shade, with necessary screws etc. complete.
37 | Twin rubber stopper |  | 2 | each | 54.58 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 109 | 109 | INR One Hundred & Nine Only | 37 | Twin rubber stopper |  | 2 | each
38 | Providing and fixing bright finished brass 100 mm mortice latch and lock, ISI marked, with six levers and a pair of anodised (anodic coating not less than grade AC 10 as per IS : 1868) aluminium lever handles of approved quality with necessary screws etc. complete. |  | 1 | each | 648.66 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 649 | 649 | INR Six Hundred & Forty Nine Only | 38 | Providing and fixing bright finished brass 100 mm mortice latch and lock, ISI marked, with six levers and a pair of anodised (anodic coating not less than grade AC 10 as per IS : 1868) aluminium lever handles of approved quality with necessary screws etc. complete. |  | 1 | each
39 | Providing and fixing partition upto ceiling height consisting of G.I. frame and required board, including providing and fixing of frame work made of special section power pressed/ roll form G.I. sheet with zinc coating of 120 gms/sqm(both side inclusive), consisting of floor and ceiling channel 50mm wide having equal flanges of 32 mm and 0.50 mm thick, fixed to the floor and ceiling at the spacing of 610 mm centre to centre with dash fastener of 12.5 mm dia meter 50 mm length or suitable anchor fastener or metal screws with nylon plugs and the studs 48 mm wide having one flange of 34 mm and other flange 36 mm and 0.50 mm thick fixed vertically within flanges of floor and ceiling channel and placed at a spacing of 610 mm centre to centre by 6 mm dia bolts and nuts, including fixing of studs along both ends of partition fixed flush to wall with suitable anchor fastener or metal screws with nylon plugs at spacing of 450 mm centre to centre, and fixing of boards to both side of frame work by 25 mm long dry wall screws on studs, floor and ceiling channels at the spacing of 300 mm centre to centre. The boards are to be fixed to the frame work with joints staggered to avoid through cracks, M.S. fixing channel of 99 mm width (0.9 mm thick having two flanges of 9.5 mm each) to be provided at the horizontal joints of two boards, fixed to the studs using metal to metal flat head screws, including jointing and finishing to a flush finish with recommended jointing compound, jointing tape, angle beads at corners (25 mm x 25 mm x 0.5 mm), joint finisher and two coats of primer suitable for board as per manufacture's specification and direction of engineer in charge all complete. | [53 empty] | 39 | Providing and fixing partition upto ceiling height consisting of G.I. frame and required board, including providing and fixing of frame work made of special section power pressed/ roll form G.I. sheet with zinc coating of 120 gms/sqm(both side inclusive), consisting of floor and ceiling channel 50mm wide having equal flanges of 32 mm and 0.50 mm thick, fixed to the floor and ceiling at the spacing of 610 mm centre to centre with dash fastener of 12.5 mm dia meter 50 mm length or suitable anchor fastener or metal screws with nylon plugs and the studs 48 mm wide having one flange of 34 mm and other flange 36 mm and 0.50 mm thick fixed vertically within flanges of floor and ceiling channel and placed at a spacing of 610 mm centre to centre by 6 mm dia bolts and nuts, including fixing of studs along both ends of partition fixed flush to wall with suitable anchor fastener or metal screws with nylon plugs at spacing of 450 mm centre to centre, and fixing of boards to both side of frame work by 25 mm long dry wall screws on studs, floor and ceiling channels at the spacing of 300 mm centre to centre. The boards are to be fixed to the frame work with joints staggered to avoid through cracks, M.S. fixing channel of 99 mm width (0.9 mm thick having two flanges of 9.5 mm each) to be provided at the horizontal joints of two boards, fixed to the studs using metal to metal flat head screws, including jointing and finishing to a flush finish with recommended jointing compound, jointing tape, angle beads at corners (25 mm x 25 mm x 0.5 mm), joint finisher and two coats of primer suitable for board as per manufacture's specification and direction of engineer in charge all complete.
40 | 75 mm overall thickness partition with 12.5 mm thick double skin fire rated Glass Reinforced Gypsum (GRG) plaster board conforming to IS: 2095: part 3 (Board with BIS certification marks) |  | 2 | sqm | 1576.19 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3152 | 3152 | INR Three Thousand One Hundred & Fifty Two Only | 40 | 75 mm overall thickness partition with 12.5 mm thick double skin fire rated Glass Reinforced Gypsum (GRG) plaster board conforming to IS: 2095: part 3 (Board with BIS certification marks) |  | 2 | sqm
41 | Providing and fixing sliding arrangement in racks/ cupboards/cabinets shutter by with stainless steel rollers to run inside C or E aluminium channel section (The payment of C or E channel shall be made separately) |  | 2 | each | 15.48 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 31 | 31 | INR Thirty One Only | 41 | Providing and fixing sliding arrangement in racks/ cupboards/cabinets shutter by with stainless steel rollers to run inside C or E aluminium channel section (The payment of C or E channel shall be made separately) |  | 2 | each
42 | Providing & Fixing decorative high pressure laminated sheet of plain / wood grain in gloss / matt/ suede finish with high density protective surface layer and reverse side of adhesive bonding quality conforming to IS : 2046 Type S, including cost of adhesive of approved quality. | [53 empty] | 42 | Providing & Fixing decorative high pressure laminated sheet of plain / wood grain in gloss / matt/ suede finish with high density protective surface layer and reverse side of adhesive bonding quality conforming to IS : 2046 Type S, including cost of adhesive of approved quality.
43 | 1.0 mm thick |  | 17.5 | sqm | 669.88 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 11723 | 11723 | INR Eleven Thousand Seven Hundred & Twenty Three Only | 43 | 1.0 mm thick |  | 17.5 | sqm
44 | STEEL WORK | [53 empty] | 44 | STEEL WORK
45 | Providing and fixing factory made ISI marked steel glazed doors, windows and ventilators, side /top /centre hung, with beading and all members such as F7D,F4B, K11 B and K12 B etc. complete of standard rolled steel sections, joints mitred and flash butt welded and sash bars tenoned and riveted, including providing and fixing of hinges, pivots, including priming coat of approved steel primer, but excluding the cost of other fittings, complete all as per approved design, (sectional weight of only steel members shall be measured for payment). | [53 empty] | 45 | Providing and fixing factory made ISI marked steel glazed doors, windows and ventilators, side /top /centre hung, with beading and all members such as F7D,F4B, K11 B and K12 B etc. complete of standard rolled steel sections, joints mitred and flash butt welded and sash bars tenoned and riveted, including providing and fixing of hinges, pivots, including priming coat of approved steel primer, but excluding the cost of other fittings, complete all as per approved design, (sectional weight of only steel members shall be measured for payment).
46 | Fixing with 15x3 mm lugs 10 cm long embedded in cement concrete block 15x10x10 cm of C.C. 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) |  | 26 | kg | 154.01 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4004 | 4004 | INR Four Thousand &Four Only | 46 | Fixing with 15x3 mm lugs 10 cm long embedded in cement concrete block 15x10x10 cm of C.C. 1:3:6 (1 Cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) |  | 26 | kg
47 | Steel work welded in built up sections/ framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer using structural steel etc. as required. | [53 empty] | 47 | Steel work welded in built up sections/ framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer using structural steel etc. as required.
48 | In stringers, treads, landings etc. of stair cases, including use of chequered plate wherever required, all complete |  | 12 | kg | 89.65 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1076 | 1076 | INR One Thousand &Seventy Six Only | 48 | In stringers, treads, landings etc. of stair cases, including use of chequered plate wherever required, all complete |  | 12 | kg
49 | Providing & fixing glass panes with putty and glazing clips in steel doors, windows, clerestory windows, all complete with : | [53 empty] | 49 | Providing & fixing glass panes with putty and glazing clips in steel doors, windows, clerestory windows, all complete with :
50 | 4.0 mm thick glass panes |  | 1.44 | sqm | 824.46 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1187 | 1187 | INR One Thousand One Hundred & Eighty Seven Only | 50 | 4.0 mm thick glass panes |  | 1.44 | sqm
51 | FLOORING | [53 empty] | 51 | FLOORING
52 | Providing and laying Vitrified tiles in different sizes (thickness to be specified by the manufacturer), with water absorption less than 0.08% and conforming to IS: 15622, of approved brand & manufacturer, in all colours and shade, in skirting, riser of steps, laid with cement based high polymer modified quick set tile adhesive (water based) conforming to IS: 15477, in average 6 mm thickness, including grouting of joints (Payment for grouting of joints to be made separately). | [53 empty] | 52 | Providing and laying Vitrified tiles in different sizes (thickness to be specified by the manufacturer), with water absorption less than 0.08% and conforming to IS: 15622, of approved brand & manufacturer, in all colours and shade, in skirting, riser of steps, laid with cement based high polymer modified quick set tile adhesive (water based) conforming to IS: 15477, in average 6 mm thickness, including grouting of joints (Payment for grouting of joints to be made separately).
53 | Size of Tile 600x600 mm |  | 8 | sqm | 1469.66 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 11757 | 11757 | INR Eleven Thousand Seven Hundred & Fifty Seven Only | 53 | Size of Tile 600x600 mm |  | 8 | sqm
54 | ROOFING | [53 empty] | 54 | ROOFING
55 | Providing and fixing tiled false ceiling of specified materials of size 595x595 mm in true horizontal level, suspended on inter locking metal grid of hot dipped galvanized steel sections ( galvanized @ 120 grams/ sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24x38 mm made from 0.30 mm thick (minimum) sheet, spaced at 1200 mm center to center and cross "T" of size 24x25 mm made of 0.30 mm thick (minimum) sheet, 1200 mm long spaced between main "T" at 600 mm center to center to form a grid of 1200x600 mm and secondary cross "T" of length 600 mm and size 24x25 mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200x600 mm panel to form grids of 600x600 mm and wall angle of size 24x24x0.3 mm and laying false ceiling tiles of approved texture in the grid including, required cutting/making, opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size 27 x 37 x 25 x1.6 mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4 mm GI adjustable rods with galvanised butterfly level clips of size 85 x 30 x 0.8 mm spaced at 1200 mm center to center along main T, bottom exposed width of 24 mm of all T-sections shall be pre-painted with polyester paint, all complete for all heights as per specifications, drawings and as directed by Engineer-in-charge. | [53 empty] | 55 | Providing and fixing tiled false ceiling of specified materials of size 595x595 mm in true horizontal level, suspended on inter locking metal grid of hot dipped galvanized steel sections ( galvanized @ 120 grams/ sqm, both side inclusive) consisting of main "T" runner with suitably spaced joints to get required length and of size 24x38 mm made from 0.30 mm thick (minimum) sheet, spaced at 1200 mm center to center and cross "T" of size 24x25 mm made of 0.30 mm thick (minimum) sheet, 1200 mm long spaced between main "T" at 600 mm center to center to form a grid of 1200x600 mm and secondary cross "T" of length 600 mm and size 24x25 mm made of 0.30 mm thick (minimum) sheet to be interlocked at middle of the 1200x600 mm panel to form grids of 600x600 mm and wall angle of size 24x24x0.3 mm and laying false ceiling tiles of approved texture in the grid including, required cutting/making, opening for services like diffusers, grills, light fittings, fixtures, smoke detectors etc. Main "T" runners to be suspended from ceiling using GI slotted cleats of size 27 x 37 x 25 x1.6 mm fixed to ceiling with 12.5 mm dia and 50 mm long dash fasteners, 4 mm GI adjustable rods with galvanised butterfly level clips of size 85 x 30 x 0.8 mm spaced at 1200 mm center to center along main T, bottom exposed width of 24 mm of all T-sections shall be pre-painted with polyester paint, all complete for all heights as per specifications, drawings and as directed by Engineer-in-charge.
56 | 12.5 mm thick square edge PVC Laminated Gypsum Tile of size 595x595 mm, made of Gypsum plasterboard, manufactured from natural gypsum as per IS 2095 part I and laminated with white 0.16mm thick fire retardant PVC film on the face side and 12micron metalized polyester on the back side with all edges sealed with the face side PVC film which goes around and wraps the edges and is bonded to the edges and the back side metalized polyester film so as to make the tile a completely sealed unit. |  | 23 | sqm | 1708.86 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 39304 | 39304 | INR Thirty Nine Thousand Three Hundred & Four Only | 56 | 12.5 mm thick square edge PVC Laminated Gypsum Tile of size 595x595 mm, made of Gypsum plasterboard, manufactured from natural gypsum as per IS 2095 part I and laminated with white 0.16mm thick fire retardant PVC film on the face side and 12micron metalized polyester on the back side with all edges sealed with the face side PVC film which goes around and wraps the edges and is bonded to the edges and the back side metalized polyester film so as to make the tile a completely sealed unit. |  | 23 | sqm
57 | FINISHING | [53 empty] | 57 | FINISHING
58 | 12 mm cement plaster of mix : | [53 empty] | 58 | 12 mm cement plaster of mix :
59 | 1:6 (1 cement: 6 coarse sand) |  | 6.2 | sqm | 258.09 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1600 | 1600 | INR One Thousand Six Hundred Only | 59 | 1:6 (1 cement: 6 coarse sand) |  | 6.2 | sqm
60 | 15 mm cement plaster on rough side of single or half brick wall of mix: | [53 empty] | 60 | 15 mm cement plaster on rough side of single or half brick wall of mix:
61 | 1:6 (1 cement: 6 coarse sand) |  | 6.2 | sqm | 297.33 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1843 | 1843 | INR One Thousand Eight Hundred & Forty Three Only | 61 | 1:6 (1 cement: 6 coarse sand) |  | 6.2 | sqm
62 | 15 mm cement plaster 1:3 (1 cement: 3 coarse sand) finished with a floating coat of neat cement on the rough side of single or half brick wall. |  | 5.5 | sqm | 382.55 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2104 | 2104 | INR Two Thousand One Hundred & Four Only | 62 | 15 mm cement plaster 1:3 (1 cement: 3 coarse sand) finished with a floating coat of neat cement on the rough side of single or half brick wall. |  | 5.5 | sqm
63 | Distempering with 1st quality acrylic distemper (ready mixed) having VOC content less than 50 gms/litre, of approved manufacturer, of required shade and colour complete, as per manufacturer's specification. | [53 empty] | 63 | Distempering with 1st quality acrylic distemper (ready mixed) having VOC content less than 50 gms/litre, of approved manufacturer, of required shade and colour complete, as per manufacturer's specification.
64 | Two or more coats on new work |  | 106 | sqm | 81.32 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8620 | 8620 | INR Eight Thousand Six Hundred & Twenty Only | 64 | Two or more coats on new work |  | 106 | sqm
65 | Finishing walls with Acrylic Smooth exterior paint of required shade : | [53 empty] | 65 | Finishing walls with Acrylic Smooth exterior paint of required shade :
66 | New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/10 sqm) |  | 6.2 | sqm | 146.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 907 | 907 | INR Nine Hundred & Seven Only | 66 | New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including priming coat of exterior primer applied @ 2.20 kg/10 sqm) |  | 6.2 | sqm
67 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade : | [53 empty] | 67 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade :
68 | Two or more coats on new work |  | 11 | sqm | 115.26 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1268 | 1268 | INR One Thousand Two Hundred & Sixty Eight Only | 68 | Two or more coats on new work |  | 11 | sqm
69 | Painting with synthetic enamel paint of approved brand and manufacture of required colour to give an even shade : | [53 empty] | 69 | Painting with synthetic enamel paint of approved brand and manufacture of required colour to give an even shade :
70 | Two or more coats on new work over an under coat of suitable shade with ordinary paint of approved brand and manufacture |  | 10 | sqm | 167.82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1678 | 1678 | INR One Thousand Six Hundred & Seventy Eight Only | 70 | Two or more coats on new work over an under coat of suitable shade with ordinary paint of approved brand and manufacture |  | 10 | sqm
71 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. |  | 106 | sqm | 108.59 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 11511 | 11511 | INR Eleven Thousand Five Hundred & Eleven Only | 71 | Providing and applying white cement based putty of average thickness 1 mm, of approved brand and manufacturer, over the plastered wall surface to prepare the surface even and smooth complete. |  | 106 | sqm
72 | Distempering with 1st quality acrylic distember (Ready mix) having VOC content less than 50 grams/ litre of approved brand and manufacture to give an even shade : | [53 empty] | 72 | Distempering with 1st quality acrylic distember (Ready mix) having VOC content less than 50 grams/ litre of approved brand and manufacture to give an even shade :
73 | Old work (one or more coats) |  | 48 | sqm | 49.8 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2390 | 2390 | INR Two Thousand Three Hundred & Ninety Only | 73 | Old work (one or more coats) |  | 48 | sqm
74 | Removing dry or oil bound distemper, water proofing cement paint and the like by scrapping, sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete. |  | 100 | sqm | 18.28 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1828 | 1828 | INR One Thousand Eight Hundred & Twenty Eight Only | 74 | Removing dry or oil bound distemper, water proofing cement paint and the like by scrapping, sand papering and preparing the surface smooth including necessary repairs to scratches etc. complete. |  | 100 | sqm
75 | REPAIRS TO BUILDING | [53 empty] | 75 | REPAIRS TO BUILDING
76 | Cutting holes of required size in brick masonry wall for fixing of exhaust fan including providing and fixing 300 mm dia PVC pipe conforming BIS-12818 and making good the same etc. complete as per direction of Engineer-in-charge. |  | 1 | each | 213.15 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 213 | 213 | INR Two Hundred & Thirteen Only | 76 | Cutting holes of required size in brick masonry wall for fixing of exhaust fan including providing and fixing 300 mm dia PVC pipe conforming BIS-12818 and making good the same etc. complete as per direction of Engineer-in-charge. |  | 1 | each
77 | Dismantling and Demolishing | [53 empty] | 77 | Dismantling and Demolishing
78 | Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead : | [53 empty] | 78 | Dismantling doors, windows and clerestory windows (steel or wood) shutter including chowkhats, architrave, holdfasts etc. complete and stacking within 50 metres lead :
79 | Of area 3 sq. metres and below |  | 7 | each | 265.41 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1858 | 1858 | INR One Thousand Eight Hundred & Fifty Eight Only | 79 | Of area 3 sq. metres and below |  | 7 | each
80 | Taking out doors, windows and clerestory window shutters (steel or wood) including stacking within 50 metres lead : | [53 empty] | 80 | Taking out doors, windows and clerestory window shutters (steel or wood) including stacking within 50 metres lead :
81 | Of area 3 sq. metres and below |  | 2 | each | 103.73 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 207 | 207 | INR Two Hundred & Seven Only | 81 | Of area 3 sq. metres and below |  | 2 | each
82 | Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead. | [53 empty] | 82 | Dismantling tile work in floors and roofs laid in cement mortar including stacking material within 50 metres lead.
83 | For thickness of tiles 10 mm to 25 mm |  | 8 | sqm | 53.05 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 424 | 424 | INR Four Hundred & Twenty Four Only | 83 | For thickness of tiles 10 mm to 25 mm |  | 8 | sqm
84 | Dismantling aluminium/ Gypsum partitions, doors, windows, fixed glazing and false ceiling including disposal of unserviceable material and stacking of serviceable material with in 50 meters lead as directed by Engineer-in-charge. |  | 46 | sqm | 40.77 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1875 | 1875 | INR One Thousand Eight Hundred & Seventy Five Only | 84 | Dismantling aluminium/ Gypsum partitions, doors, windows, fixed glazing and false ceiling including disposal of unserviceable material and stacking of serviceable material with in 50 meters lead as directed by Engineer-in-charge. |  | 46 | sqm
85 | SANITARY INSTALLATIONS | [53 empty] | 85 | SANITARY INSTALLATIONS
86 | Providing and fixing white vitreous china laboratory sink including making all connections excluding cost of fittings : | [53 empty] | 86 | Providing and fixing white vitreous china laboratory sink including making all connections excluding cost of fittings :
87 | Size 600x450x200 mm |  | 1 | each | 3060.19 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3060 | 3060 | INR Three Thousand &Sixty Only | 87 | Size 600x450x200 mm |  | 1 | each
88 | Providing and fixing P.V.C. waste pipe for sink or wash basin including P.V.C. waste fittings complete. | [53 empty] | 88 | Providing and fixing P.V.C. waste pipe for sink or wash basin including P.V.C. waste fittings complete.
89 | Flexible pipe | [53 empty] | 89 | Flexible pipe
90 | 32 mm dia |  | 1 | each | 91.49 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 91 | 91 | INR Ninety One Only | 90 | 32 mm dia |  | 1 | each
91 | WATER SUPPLY | [53 empty] | 91 | WATER SUPPLY
92 | Providing and fixing G.I. pipes complete with G.I. fittings and clamps, i/c cutting and making good the walls etc. Internal work - Exposed on wall | [53 empty] | 92 | Providing and fixing G.I. pipes complete with G.I. fittings and clamps, i/c cutting and making good the walls etc. Internal work - Exposed on wall
93 | 20 mm dia nominal bore |  | 6 | metre | 327.36 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1964 | 1964 | INR One Thousand Nine Hundred & Sixty Four Only | 93 | 20 mm dia nominal bore |  | 6 | metre
94 | 40 mm dia nominal bore |  | 17 | metre | 635.82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 10809 | 10809 | INR Ten Thousand Eight Hundred & Nine Only | 94 | 40 mm dia nominal bore |  | 17 | metre
95 | Providing and fixing G.I. Pipes complete with G.I. fittings and clamps, i/c making good the walls etc. concealed pipe, including painting with anti corrosive bitumastic paint, cutting chases and making good the wall : | [53 empty] | 95 | Providing and fixing G.I. Pipes complete with G.I. fittings and clamps, i/c making good the walls etc. concealed pipe, including painting with anti corrosive bitumastic paint, cutting chases and making good the wall :
96 | 15 mm dia nominal bore |  | 2 | metre | 425.43 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 851 | 851 | INR Eight Hundred & Fifty One Only | 96 | 15 mm dia nominal bore |  | 2 | metre
97 | Making connection of G.I. distribution branch with G.I. main of following sizes by providing and fixing tee, including cutting and threading the pipe etc. complete : | [53 empty] | 97 | Making connection of G.I. distribution branch with G.I. main of following sizes by providing and fixing tee, including cutting and threading the pipe etc. complete :
98 | 25 to 40 mm nominal bore |  | 1 | each | 663.83 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 664 | 664 | INR Six Hundred & Sixty Four Only | 98 | 25 to 40 mm nominal bore |  | 1 | each
99 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) : | [53 empty] | 99 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end) :
100 | 20 mm nominal bore |  | 1 | each | 404.87 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 405 | 405 | INR Four Hundred & Five Only | 100 | 20 mm nominal bore |  | 1 | each
101 | Providing and fixing G.I. Union in existing G.I. pipe line, cutting and threading the pipe and making long screws, including excavation, refilling the earth or cutting of wall and making good the same complete wherever required : | [53 empty] | 101 | Providing and fixing G.I. Union in existing G.I. pipe line, cutting and threading the pipe and making long screws, including excavation, refilling the earth or cutting of wall and making good the same complete wherever required :
102 | 20 mm nominal bore |  | 2 | each | 622.27 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1245 | 1245 | INR One Thousand Two Hundred & Forty Five Only | 102 | 20 mm nominal bore |  | 2 | each
103 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms. | [53 empty] | 103 | Providing and fixing C.P. brass long body bib cock of approved quality conforming to IS standards and weighing not less than 690 gms.
104 | 15 mm nominal bore |  | 2 | each | 621.13 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1242 | 1242 | INR One Thousand Two Hundred & Forty Two Only | 104 | 15 mm nominal bore |  | 2 | each
105 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS:8931. | [53 empty] | 105 | Providing and fixing C.P. brass stop cock (concealed) of standard design and of approved make conforming to IS:8931.
106 | 15 mm nominal bore |  | 1 | each | 521.48 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 521 | 521 | INR Five Hundred & Twenty One Only | 106 | 15 mm nominal bore |  | 1 | each
107 | Cutting holes up to 30x30 cm in walls including making good the same: | [53 empty] | 107 | Cutting holes up to 30x30 cm in walls including making good the same:
108 | With common burnt clay F.P.S. (non modular) bricks |  | 2 | each | 317.76 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 636 | 636 | INR Six Hundred & Thirty Six Only | 108 | With common burnt clay F.P.S. (non modular) bricks |  | 2 | each
109 | Cutting holes up to 15x15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), including finishing complete so as to make it leak proof. |  | 1 | each | 330.64 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 331 | 331 | INR Three Hundred & Thirty One Only | 109 | Cutting holes up to 15x15 cm in R.C.C. floors and roofs for passing drain pipe etc. and repairing the hole after insertion of drain pipe etc. with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), including finishing complete so as to make it leak proof. |  | 1 | each
110 | ALUMINIUM WORK | [53 empty] | 110 | ALUMINIUM WORK
111 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) : | [53 empty] | 111 | Providing and fixing aluminium work for doors, windows, ventilators and partitions with extruded built up standard tubular sections/ appropriate Z sections and other sections of approved make conforming to IS: 733 and IS: 1285, fixing with dash fasteners of required dia and size, including necessary filling up the gaps at junctions, i.e. at top, bottom and sides with required EPDM rubber/ neoprene gasket etc. Aluminium sections shall be smooth, rust free, straight, mitred and jointed mechanically wherever required including cleat angle, Aluminium snap beading for glazing / paneling, C.P. brass / stainless steel screws, all complete as per architectural drawings and the directions of Engineer-in-charge. (Glazing, paneling and dash fasteners to be paid for separately) :
112 | For fixed portion | [53 empty] | 112 | For fixed portion
113 | Anodised aluminium (anodised transparent or dyed to required shade according to IS: 1868, Minimum anodic coating of grade AC 15) |  | 6.25 | kg | 380.49 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2378 | 2378 | INR Two Thousand Three Hundred & Seventy Eight Only | 113 | Anodised aluminium (anodised transparent or dyed to required shade according to IS: 1868, Minimum anodic coating of grade AC 15) |  | 6.25 | kg
114 | Providing and fixing 12 mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS: 12823 Grade l Type ll, in panelling fixed in aluminum doors, windows shutters and partition frames with C.P. brass / stainless steel screws etc. complete as per architectural drawings and directions of engineer- in-charge. | [53 empty] | 114 | Providing and fixing 12 mm thick prelaminated particle board flat pressed three layer or graded wood particle board conforming to IS: 12823 Grade l Type ll, in panelling fixed in aluminum doors, windows shutters and partition frames with C.P. brass / stainless steel screws etc. complete as per architectural drawings and directions of engineer- in-charge.
115 | Pre-laminated particle board with decorative lamination on one side and balancing lamination on other side |  | 8.75 | sqm | 846.21 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7404 | 7404 | INR Seven Thousand Four Hundred & Four Only | 115 | Pre-laminated particle board with decorative lamination on one side and balancing lamination on other side |  | 8.75 | sqm
116 | Providing and fixing Brass 100mm mortice latch and lock with 6 levers without pair of handles (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete. |  | 1 | each | 394.17 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 394 | 394 | INR Three Hundred & Ninety Four Only | 116 | Providing and fixing Brass 100mm mortice latch and lock with 6 levers without pair of handles (best make of approved quality) for aluminium doors including necessary cutting and making good etc. complete. |  | 1 | each
117 | Providing and fixing aluminium round shape handle of outer dia 100 mm with SS screws etc. complete as per direction of Engineer-in- charge | [53 empty] | 117 | Providing and fixing aluminium round shape handle of outer dia 100 mm with SS screws etc. complete as per direction of Engineer-in- charge
118 | Anodized (AC 15 ) aluminium |  | 4 | each | 77.82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 311 | 311 | INR Three Hundred & Eleven Only | 118 | Anodized (AC 15 ) aluminium |  | 4 | each
119 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required. | [53 empty] | 119 | Supplying and drawing following sizes of FRLS PVC insulated copper conductor, single core cable in the existing surface/ recessed steel/ PVC conduit as required.
120 | 3 x 1.5 sq. mm |  | 50 | Metre | 83.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4165 | 4165 | INR Four Thousand One Hundred & Sixty Five Only | 120 | 3 x 1.5 sq. mm |  | 50 | Metre
121 | 3 x 2.5 sq. mm |  | 250 | Metre | 120.12 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 30030 | 30030 | INR Thirty Thousand &Thirty Only | 121 | 3 x 2.5 sq. mm |  | 250 | Metre
122 | 3 x 4 sq. mm |  | 200 | Metre | 180.62 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 36124 | 36124 | INR Thirty Six Thousand One Hundred & Twenty Four Only | 122 | 3 x 4 sq. mm |  | 200 | Metre
123 | 2 x 16 sq.mm. |  | 20 | Meter | 533.98 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 10680 | 10680 | INR Ten Thousand Six Hundred & Eighty Only | 123 | 2 x 16 sq.mm. |  | 20 | Meter
124 | 3 x 16 sq.mm. |  | 25 | Meter | 781.24 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 19531 | 19531 | INR Nineteen Thousand Five Hundred & Thirty One Only | 124 | 3 x 16 sq.mm. |  | 25 | Meter
125 | Supply and fixing of 32 x 20 mm DLP mini- trunking white-system with independent cover etc. as required complete. |  | 20 | Meter | 228.85 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4577 | 4577 | INR Four Thousand Five Hundred & Seventy Seven Only | 125 | Supply and fixing of 32 x 20 mm DLP mini- trunking white-system with independent cover etc. as required complete. |  | 20 | Meter
126 | Supply and fixing of 105 x 50 mm DLP trunking white-system but without cover and partition etc. as required complete. |  | 20 | Meter | 980.27 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 19605 | 19605 | INR Nineteen Thousand Six Hundred & Five Only | 126 | Supply and fixing of 105 x 50 mm DLP trunking white-system but without cover and partition etc. as required complete. |  | 20 | Meter
127 | Supply and fixing of following accessories suitable for 105 mm x 50 mm size plastic trunking white system. | [53 empty] | 127 | Supply and fixing of following accessories suitable for 105 mm x 50 mm size plastic trunking white system.
128 | 85 mm flexible cover |  | 20 | Meter | 432.27 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8645 | 8645 | INR Eight Thousand Six Hundred & Forty Five Only | 128 | 85 mm flexible cover |  | 20 | Meter
129 | End cap |  | 4 | Nos. | 194.65 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 779 | 779 | INR Seven Hundred & Seventy Nine Only | 129 | End cap |  | 4 | Nos.
130 | Internal angles- adjustable from 80°-100° |  | 5 | Nos. | 539.24 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2696 | 2696 | INR Two Thousand Six Hundred & Ninety Six Only | 130 | Internal angles- adjustable from 80°-100° |  | 5 | Nos.
131 | external angles- adjustable from 60°-120° |  | 5 | Nos. | 551.51 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2758 | 2758 | INR Two Thousand Seven Hundred & Fifty Eight Only | 131 | external angles- adjustable from 60°-120° |  | 5 | Nos.
132 | flat junction |  | 2 | Nos. | 939.06 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1878 | 1878 | INR One Thousand Eight Hundred & Seventy Eight Only | 132 | flat junction |  | 2 | Nos.
133 | flat angles |  | 2 | Nos. | 762.82 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1526 | 1526 | INR One Thousand Five Hundred & Twenty Six Only | 133 | flat angles |  | 2 | Nos.
134 | separation partitions |  | 10 | Meter | 260.41 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2604 | 2604 | INR Two Thousand Six Hundred & Four Only | 134 | separation partitions |  | 10 | Meter
135 | Joints for 85mm width cover |  | 10 | Nos. | 224.46 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2245 | 2245 | INR Two Thousand Two Hundred & Forty Five Only | 135 | Joints for 85mm width cover |  | 10 | Nos.
136 | base joints |  | 18 | Nos. | 90.31 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1626 | 1626 | INR One Thousand Six Hundred & Twenty Six Only | 136 | base joints |  | 18 | Nos.
137 | Supplying, installation of Clip-on frame with finishing plate for 85mm cover for DLP plastic trunking 105mm x 50mm etc. as reqd. | [53 empty] | 137 | Supplying, installation of Clip-on frame with finishing plate for 85mm cover for DLP plastic trunking 105mm x 50mm etc. as reqd.
138 | 3 module |  | 11 | Nos. | 301.62 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3318 | 3318 | INR Three Thousand Three Hundred & Eighteen Only | 138 | 3 module |  | 11 | Nos.
139 | 6 module |  | 32 | Nos. | 404.21 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 12935 | 12935 | INR Twelve Thousand Nine Hundred & Thirty Five Only | 139 | 6 module |  | 32 | Nos.
140 | Supplying and fixing following modular switch/ socket on the existing clip-on frame fixed on 85mm cover of 105 x 50 mm DLP plastic trunking including connections etc. as required complete. | [53 empty] | 140 | Supplying and fixing following modular switch/ socket on the existing clip-on frame fixed on 85mm cover of 105 x 50 mm DLP plastic trunking including connections etc. as required complete.
141 | 6 A switch |  | 71 | No. | 240.25 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 17058 | 17058 | INR Seventeen Thousand &Fifty Eight Only | 141 | 6 A switch |  | 71 | No.
142 | 20 A switch |  | 14 | No. | 427.01 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5978 | 5978 | INR Five Thousand Nine Hundred & Seventy Eight Only | 142 | 20 A switch |  | 14 | No.
143 | 6 A pin 2/3 pin socket outlet |  | 57 | No. | 280.58 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 15993 | 15993 | INR Fifteen Thousand Nine Hundred & Ninety Three Only | 143 | 6 A pin 2/3 pin socket outlet |  | 57 | No.
144 | 6/16 A 3 pin socket outlet |  | 14 | No. | 547.13 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 7660 | 7660 | INR Seven Thousand Six Hundred & Sixty Only | 144 | 6/16 A 3 pin socket outlet |  | 14 | No.
145 | Supply and fixing of following LED light fixture with efficiency >100 lumen/ watt, P.F. >0.95, THD<10%, Electronic driver, LED lamp, reflector, diffuser, MS body/housing holder etc. complete with all fixing accessories and lamp as required complete. | [53 empty] | 145 | Supply and fixing of following LED light fixture with efficiency >100 lumen/ watt, P.F. >0.95, THD<10%, Electronic driver, LED lamp, reflector, diffuser, MS body/housing holder etc. complete with all fixing accessories and lamp as required complete.
146 | 36 watt recess mounting LED light fixture 600 x 600 mm |  | 10 | Nos. | 4658.48 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 46585 | 46585 | INR Forty Six Thousand Five Hundred & Eighty Five Only | 146 | 36 watt recess mounting LED light fixture 600 x 600 mm |  | 10 | Nos.
147 | Laying UTP cable enhanced cat 5/cat 6 cable in existing steel conduit pipe/GI pipe/ raceway / RCC pipe as reqd. the cost shall also include numbering of networking wire from room to rack as reqd. (wire will be supplied by dept) |  | 150 | Meter | 19.29 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2894 | 2894 | INR Two Thousand Eight Hundred & Ninety Four Only | 147 | Laying UTP cable enhanced cat 5/cat 6 cable in existing steel conduit pipe/GI pipe/ raceway / RCC pipe as reqd. the cost shall also include numbering of networking wire from room to rack as reqd. (wire will be supplied by dept) |  | 150 | Meter
148 | Fixing of RJ-45 modular box with cover plate or I/o box for internet on surface/ recessed cutting the wall making good the same as required. ( box and cover plate will be supplied by dept.) |  | 20 | Nos. | 81.54 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1631 | 1631 | INR One Thousand Six Hundred & Thirty One Only | 148 | Fixing of RJ-45 modular box with cover plate or I/o box for internet on surface/ recessed cutting the wall making good the same as required. ( box and cover plate will be supplied by dept.) |  | 20 | Nos.
149 | Supplying and fixing following rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required. | [53 empty] | 149 | Supplying and fixing following rating, 240/415 V, 10 kA, "C" curve, miniature circuit breaker suitable for inductive load of following poles in the existing MCB DB complete with connections, testing and commissioning etc. as required.
150 | Single pole 5 A to 32 A |  | 8 | No. | 224.46 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1796 | 1796 | INR One Thousand Seven Hundred & Ninety Six Only | 150 | Single pole 5 A to 32 A |  | 8 | No.
151 | Double Pole (40A-63A) |  | 2 | Nos. | 1574.75 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3150 | 3150 | INR Three Thousand One Hundred & Fifty Only | 151 | Double Pole (40A-63A) |  | 2 | Nos.
152 | Four Pole (40A-63A) |  | 1 | Nos. | 3038.14 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 3038 | 3038 | INR Three Thousand &Thirty Eight Only | 152 | Four Pole (40A-63A) |  | 1 | Nos.
153 | S & F metal enclosure suitable for DP/TPN MCB / DP ELCB on surface or recessed etc as reqd. |  | 2 | Nos. | 910.13 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1820 | 1820 | INR One Thousand Eight Hundred & Twenty Only | 153 | S & F metal enclosure suitable for DP/TPN MCB / DP ELCB on surface or recessed etc as reqd. |  | 2 | Nos.
154 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/lsolator) | [53 empty] | 154 | Supplying and fixing following way, single pole and neutral, sheet steel, MCB distribution board, 240 V, on surface/ recess, complete with tinned copper bus bar, neutral bus bar, earth bar, din bar, interconnections, powder painted including earthing etc. as required. (But without MCB/RCCB/lsolator)
155 | 8 way , Double door |  | 1 | No. | 2256.03 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2256 | 2256 | INR Two Thousand Two Hundred & Fifty Six Only | 155 | 8 way , Double door |  | 1 | No.
156 | Supply, Installation, Testing and Commissioning of 1200 mm sweep, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, Power Factor not less than 0.9, Service Value (CM/M/W) minimum 6.00, Air delivery minimum 210 Cum/Min, 350 RPM (tolerance as per IS : 374-2019), THD less than 10%, remote or electronic regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75 degree C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase AC Supply, earthing etc. complete as required. |  | 4 | Each | 2393.69 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 9575 | 9575 | INR Nine Thousand Five Hundred & Seventy Five Only | 156 | Supply, Installation, Testing and Commissioning of 1200 mm sweep, BEE 5 star rated, ceiling fan with Brush Less Direct Current (BLDC) Motor, class of insulation: B, 3 nos. blades, 30 cm long down rod, 2 nos. canopies, shackle kit, safety rope, copper winding, Power Factor not less than 0.9, Service Value (CM/M/W) minimum 6.00, Air delivery minimum 210 Cum/Min, 350 RPM (tolerance as per IS : 374-2019), THD less than 10%, remote or electronic regulator unit for speed control and all remaining accessories including safety pin, nut bolts, washers, temperature rise=75 degree C (max.), insulation resistance more than 2 mega ohm, suitable for 230 V, 50 Hz, single phase AC Supply, earthing etc. complete as required. |  | 4 | Each
157 | S & F following size of steel flexible pipe along with the accessories on surface etc as required | [53 empty] | 157 | S & F following size of steel flexible pipe along with the accessories on surface etc as required
158 | 25 mm |  | 8 | Meter | 71.02 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 568 | 568 | INR Five Hundred & Sixty Eight Only | 158 | 25 mm |  | 8 | Meter
159 | 32 mm |  | 8 | Meter | 83.3 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 666 | 666 | INR Six Hundred & Sixty Six Only | 159 | 32 mm |  | 8 | Meter
160 | S&F, Copper tube / reducer/ lug terminals suitable for following size of conductor. | [53 empty] | 160 | S&F, Copper tube / reducer/ lug terminals suitable for following size of conductor.
161 | 6 /10/16 Sq.mm. |  | 22 | Nos. | 33.32 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 733 | 733 | INR Seven Hundred & Thirty Three Only | 161 | 6 /10/16 Sq.mm. |  | 22 | Nos.
162 | Dismantling, disconnecting old damaged unserviceable fl fitting/ exhaust fan/ ceiling fan/ bulkhead fitting with bracket etc. as reqd. and depositing in sectional store. |  | 14 | Nos. | 96.45 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1350 | 1350 | INR One Thousand Three Hundred & Fifty Only | 162 | Dismantling, disconnecting old damaged unserviceable fl fitting/ exhaust fan/ ceiling fan/ bulkhead fitting with bracket etc. as reqd. and depositing in sectional store. |  | 14 | Nos.
163 | Dismantling the old conduit pipe/wood batten of all sizes from surface/recessed & making good the damages I/c filling the holes of the surface etc as reqd. and depositing it in sectional store. |  | 20 | Meter | 31.57 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 631 | 631 | INR Six Hundred & Thirty One Only | 163 | Dismantling the old conduit pipe/wood batten of all sizes from surface/recessed & making good the damages I/c filling the holes of the surface etc as reqd. and depositing it in sectional store. |  | 20 | Meter
164 | Fixing 20/25/32 mm conduit pipe/ DLP on surface with clamp/in recessed only conduit pipe supplied by department.(Free of cost) |  | 20 | Meter | 115.74 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2315 | 2315 | INR Two Thousand Three Hundred & Fifteen Only | 164 | Fixing 20/25/32 mm conduit pipe/ DLP on surface with clamp/in recessed only conduit pipe supplied by department.(Free of cost) |  | 20 | Meter
165 | Dismantling concealed & damaged DB/TPN Switches/starter/ loose wire boxes along with all accessories and depositing the same in the sectional store repairing the damages as reqd complete. |  | 1 | Nos. | 244.63 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 245 | 245 | INR Two Hundred & Forty Five Only | 165 | Dismantling concealed & damaged DB/TPN Switches/starter/ loose wire boxes along with all accessories and depositing the same in the sectional store repairing the damages as reqd complete. |  | 1 | Nos.
166 | Fixing MS Box up to 250 x 300 x100 mm including pole fuse box and painting. with enamel paint as reqd |  | 1 | Nos. | 296.36 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 296 | 296 | INR Two Hundred & Ninety Six Only | 166 | Fixing MS Box up to 250 x 300 x100 mm including pole fuse box and painting. with enamel paint as reqd |  | 1 | Nos.
167 | Fixing of Network rack on steel fastener including cartage from store to site as reqd complete. |  | 1 | Nos. | 261.29 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 261 | 261 | INR Two Hundred & Sixty One Only | 167 | Fixing of Network rack on steel fastener including cartage from store to site as reqd complete. |  | 1 | Nos.
168 | Supplying and drawing of UTP 4 pair CAT 6 LAN Cable in the existing surface/ recessed Steel/ PVC conduit as required. | [53 empty] | 168 | Supplying and drawing of UTP 4 pair CAT 6 LAN Cable in the existing surface/ recessed Steel/ PVC conduit as required.
169 | 1 run of cable |  | 50 | Metre | 49.98 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2499 | 2499 | INR Two Thousand Four Hundred & Ninety Nine Only | 169 | 1 run of cable |  | 50 | Metre
170 | 2 run of cable |  | 50 | Metre | 84.17 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 4209 | 4209 | INR Four Thousand Two Hundred & Nine Only | 170 | 2 run of cable |  | 50 | Metre
171 | 3 run of cable |  | 50 | Metre | 117.49 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5875 | 5875 | INR Five Thousand Eight Hundred & Seventy Five Only | 171 | 3 run of cable |  | 50 | Metre
Total in Figures | [51 empty] | 526503 | #REF! | Five Lakh Twenty Six Thousand Five Hundred & Three Only | Total in Figures |  | 29911889
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | INR Zero Only | Quoted Rate in Figures |  | Excess (+)
Quoted Rate in Words |  | INR Zero Only | [52 empty] | Quoted Rate in Words |  | INR Zero Only

## Macros
Please Enable Macros to View BoQ information