RESULTS OF THE WATER QUALITY PARAMETERS OF the institute

(SAMPLING DATE 26/08/20)

| Parameters | Permissible Limit | Maximum Limit | P1 | P2 | P3 | P7 | P8 | P11 | P12 | P13 | P14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 6.5 to 8.5 | No relaxation | 8.29 | 8.33 | 8.43 | 8.35 | 8.27 | 8.42 | 8.45 | 8.42 | 8.34 |
| TDS (mg/l) | 500 | 2000 | 498 | 518 | 446 | 652 | 761 | 658 | 390 | 576 | 645 |
| Hardness (as CaCO3) (mg/l) | 200 | 600 | 140 | 120 | 100 | 120 | 90 | 140 | 100 | 110 | 120 |
| Alkalinity(as CaCO3) (mg/l) | 200 | 600 | 340 | 440 | 340 | 290 | 320 | 330 | 350 | 310 | 320 |
| Nitrate (mg/l) | 45 | No relaxation | 0.14 | 0.27 | 0.08 | 0.06 | 0.08 | 0.19 | 0.14 | 0.11 | 0.06 |
| Sulfate (mg/l) | 200 | 400 | 28.07 | 14.74 | 21.18 | 29.64 | 31.85 | 38.76 | 45.28 | 31.78 | 18.66 |
| Fluoride (mg/l) | 1 | 1.5 | 0.728 | 0.819 | 0.798 | 0.564 | 0.644 | 0.783 | 0.758 | 0.812 | 0.779 |
| Chloride (mg/l) | 250 | 1000 | 175 | 100 | 130 | 295 | 340 | 300 | 110 | 225 | 285 |
| Turbidity (NTU) | 5 | 10 | 0.001 | 0.001 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Arsenic (mg/l) | 0.01 | 0.05 | 0.0029 | 0.0028 | 0.0024 | 0.0035 | 0.0038 | 0.0025 | 0.0032 | 0.0031 | 0.0027 |
| Copper (mg/l) | 0.05 | 1.5 | 0.0021 | 0.0017 | 0.0016 | 0.0027 | 0.0051 | 0.0031 | 0.0016 | 0.0026 | 0.0031 |
| Cadmium (mg/l) | 0.003 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.05 | No relaxation | 0.0042 | 0.0071 | 0.0052 | 0.0049 | 0.0031 | 0.0058 | 0.0051 | 0.0046 | 0.0045 |
| Lead (mg/l) | 0.01 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.3 | No relaxation | 0.28 | 0.26 | 0.16 | 0.10 | 0.13 | 0.11 | 0.16 | 0.19 | 0.16 |
| Zinc (mg/l) | 5 | 15 | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Sampling Locations:  P1 – Opp. Type 2 shop-C  near water tank, P2- End of lane 37 near house 4098, P3 – Behind Helicopter building, P7 -  Near water tank and main entrance of  VH-Extension , type-1,   P-8 Near Health Centre, P-11 Hall 10 back side,  P-12 - Near about 150 M of  P-2 (end of lane-36), P13 – Near Visiting Faculty Apartment, P14 Near Hall 12,

BDL Below Detection Limit;  NTU – Nephelometric Turbidity Unit; cfu-  Colony forming Units in 100 ml of the sample

Detection Limits Pb 0.0001 mg/l, Cu 0.0001 mg/l , Cr 0.0005 mg/l ,Fe 0.0001 mg/l , Cd 0.0004 mg/l, As 0.0001 mg/l, Zn 0.0005 mg/l