RESULTS OF THE WATER QUALITY PARAMETERS OF the institute

(SAMPLING DATE 25/08/21)

| Parameters | Permissible Limit | Maximum Limit | P1 | P3 | P7 | P8 | P11 | P12 | P13 | P14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 6.5 to 8.5 | No relaxation | 8.19 | 8.41 | 8.29 | 8.38 | 8.23 | 8.42 | 8.37 | 8.34 |
| TDS (mg/l) | 500 | 2000 | 501 | 439 | 655 | 755 | 650 | 407 | 560 | 638 |
| Hardness (as CaCO3) (mg/l) | 200 | 600 | 110 | 130 | 150 | 140 | 130 | 100 | 150 | 120 |
| Alkalinity(as CaCO3) (mg/l) | 200 | 600 | 310 | 320 | 260 | 250 | 260 | 320 | 270 | 250 |
| Nitrate (mg/l) | 45 | No relaxation | 0.11 | 0.09 | 0.06 | 0.07 | 0.12 | 0.14 | 0.05 | 0.09 |
| Sulfate (mg/l) | 200 | 400 | 34.21 | 27.81 | 35.44 | 42.53 | 37.72 | 39.54 | 41.11 | 29.85 |
| Fluoride (mg/l) | 1 | 1.5 | 0.682 | 0.781 | 0.628 | 0.594 | 0.625 | 0.784 | 0.672 | 0.674 |
| Chloride (mg/l) | 250 | 1000 | 160 | 125 | 275 | 300 | 285 | 210 | 205 | 270 |
| Turbidity (NTU) | 5 | 10 | 0.001 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Arsenic (mg/l) | 0.01 | 0.05 | 0.0027 | 0.0028 | 0.0021 | 0.0034 | 0.0028 | 0.0034 | 0.0027 | 0.0029 |
| Copper (mg/l) | 0.05 | 1.5 | 0.0016 | 0.0019 | 0.0027 | 0.0029 | 0.0027 | 0.0016 | 0.0023 | 0.0021 |
| Cadmium (mg/l) | 0.003 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.05 | No relaxation | 0.0026 | 0.0017 | 0.0023 | 0.0016 | 0.0018 | 0.0017 | 0.0014 | 0.0018 |
| Lead (mg/l) | 0.01 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.3 | No relaxation | 0.17 | 0.18 | 0.13 | 0.11 | 0.10 | 0.17 | 0.14 | 0.16 |
| Zinc (mg/l) | 5 | 15 | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Sampling Locations:  P1 – Opp. Type 2 shop-C  near water tank, P3 – Behind Helicopter building, P7 -  Near water tank and main entrance of  VH-Extension , type-1, P-8 Near Health Centre, P-11 Hall 10 back side,  P-12 - Near about 150 M of  P-2 (end of lane-36), P13 – Near Visiting Faculty Apartment, P14 Near Hall 12,

BDL Below Detection Limit;  NTU – Nephelometric Turbidity Unit; cfu-  Colony forming Units in 100 ml of the sample

Detection Limits Pb 0.0001 mg/l, Cu 0.0001 mg/l , Cr 0.0005 mg/l ,Fe 0.0001 mg/l , Cd 0.0004 mg/l, As 0.0001 mg/l, Zn 0.0005 mg/l