RESULTS OF THE WATER QUALITY PARAMETERS OF the institute

(SAMPLING DATE 24/02/20)

TABLE 1- PUMPS

| Parameters | Permissible Limit | Maximum Limit | P1 | P2 | P3 | P7 | P8 | P11 | P12 | P13 | P14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 6.5 to 8.5 | No relaxation | 8.27 | 8.37 | 8.06 | 8.29 | 8.04 | 8.37 | 8.31 | 8.15 | 8.21 |
| TDS (mg/l) | 500 | 2000 | 476 | 394 | 482 | 625 | 740 | 639 | 392 | 481 | 625 |
| Hardness (as CaCO3) (mg/l) | 200 | 600 | 100 | 180 | 120 | 140 | 200 | 190 | 110 | 180 | 160 |
| Alkalinity (as CaCO3) (mg/l) | 200 | 600 | 290 | 300 | 280 | 280 | 210 | 220 | 300 | 280 | 240 |
| Nitrate (mg/l) | 45 | No relaxation | 0.04 | 0.28 | 0.05 | 0.06 | 0.07 | 0.08 | 0.09 | 0.04 | 0.07 |
| Sulfate (mg/l) | 200 | 400 | 54.73 | 56.72 | 32.54 | 48.94 | 58.36 | 45.42 | 49.89 | 53.05 | 58.84 |
| Fluoride (mg/l) | 1 | 1.5 | 0.879 | 0.880 | 0.752 | 0.672 | 0.655 | 0.746 | 0.406 | 0.826 | 0.689 |
| Chloride (mg/l) | 250 | 1000 | 145 | 45 | 135 | 300 | 260 | 295 | 90 | 220 | 240 |
| Turbidity (NTU) | 5 | 10 | 0 | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Arsenic (mg/l) | 0.01 | 0.05 | 0.0015 | 0.0020 | 0.0014 | 0.0012 | 0.0013 | 0.0012 | 0.0022 | 0.0013 | 0.0004 |
| Copper (mg/l) | 0.05 | 1.5 | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Cadmium (mg/l) | 0.003 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.05 | No relaxation | 0.0053 | 0.0047 | 0.0031 | 0.0046 | 0.0042 | 0.0041 | 0.0062 | 0.0048 | 0.0043 |
| Lead (mg/l) | 0.01 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.3 | 1 | 0.17 | 0.14 | 0.18 | 0.25 | 0.17 | 0.37 | 0.14 | 0.16 | 0.23 |
| Zinc (mg/l) | 5 | 15 | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

TABLE 2 - VARIOUS HOSTELS

| Parameters | Hall 1 | Hall 2 | Hall 3 | Hall 4 | Hall 5 | Hall 7 | Hall 8 | Hall 9 | Hall 10 | Hall 11 | Hall 12 | Hall 13 | GH 1 | GH2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 8.25 | 7.92 | 8.28 | 8.22 | 8.24 | 8.29 | 7.88 | 7.98 | 8.26 | 7.62 | 7.61 | 8.19 | 8.23 | 8.35 |
| TDS (mg/l) | 756 | 224 | 679 | 761 | 694 | 655 | 55.7 | 246 | 669 | 79.7 | 73.4 | 632 | 763 | 763 |
| Hardness (as CaCO3) (mg/l) | 120 | 80 | 130 | 160 | 130 | 140 | 90 | 100 | 130 | 80 | 100 | 200 | 180 | 140 |
| Alkalinity (as CaCO3) (mg/l) | 220 | 100 | 210 | 310 | 230 | 250 | 80 | 120 | 230 | 50 | 70 | 250 | 330 | 300 |
| Nitrate (mg/l) | 0.18 | 0.06 | 0.04 | 0.09 | 0.03 | 0.29 | 0.06 | 0.04 | 0.10 | 0.04 | 0.03 | 0.02 | 0.03 | 0.01 |
| Sulfate (mg/l) | 55.04 | 21.68 | 19.21 | 35.36 | 41.94 | 57.68 | 17.57 | 33.89 | 28.05 | 7.78 | 4.26 | 41.15 | 37.63 | 69.26 |
| Fluoride (mg/l) | 0.564 | 0.215 | 0.623 | 0.577 | 0.680 | 0.781 | 0.039 | 0.242 | 0.669 | 0.055 | 0.071 | 0.647 | 0.602 | 0.633 |
| Chloride (mg/l) | 295 | 115 | 265 | 305 | 280 | 275 | 30 | 100 | 295 | 45 | 30 | 250 | 300 | 295 |
| Turbidity (NTU) | 0.002 | 0.001 | 0.001 | 0 | 0 | 0 | 0 | 0.01 | 0 | 0.02 | 0.001 | 0.001 | 0.01 | 0.01 |
| Arsenic (mg/l) | 0.0008 | 0.0006 | 0.0011 | 0.0007 | 0.0007 | 0.0017 | 0.0001 | BDL | 0.0009 | 0.0002 | BDL | 0.0007 | 0.0009 | 0.0007 |
| Copper (mg/l) | 0.0007 | 0.0011 | 0.0005 | 0.0011 | 0.0020 | 0.0013 | 0.0004 | 0.0015 | 0.0010 | 0.0043 | 0.0012 | 0.0007 | 0.0019 | 0.0011 |
| Cadmium (mg/l) | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.0043 | 0.0024 | 0.0037 | 0.0031 | 0.0038 | 0.0028 | 0.0011 | 0.0020 | 0.0038 | 0.0013 | 0.0010 | 0.0042 | 0.0047 | 0.0038 |
| Lead (mg/l) | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.363 | 0.1458 | 0.2694 | 0.1422 | 0.2978 | 0.2604 | 0.0817 | 0.1136 | 0.2502 | 0.1246 | 0.0952 | 0.2469 | 0.2584 | 0.2716 |
| Zinc (mg/l) | 0.0166 | 0.0226 | 0.0130 | 0.1827 | 0.1225 | 0.0284 | 0.0371 | 0.0137 | 0.1007 | 0.0168 | 0.0166 | 0.0467 | 0.0244 | 0.0239 |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Table 2 Hostels Contd..

| Parameters | New RA | Old RA | VH | HC | New SBRA | Old SBRA |
| --- | --- | --- | --- | --- | --- | --- |
| pH | 7.19 | 8.12 | 7.81 | 8.26 | 7.68 | 8.18 |
| TDS (mg/l) | 58.8 | 702 | 136 | 609 | 112 | 610 |
| Hardness (as CaCO3) (mg/l) | 80 | 150 | 70 | 150 | 100 | 140 |
| Alkalinity (as CaCO3) (mg/l) | 70 | 210 | 100 | 230 | 120 | 240 |
| Nitrate (mg/l) | 0.04 | 0.05 | 0.02 | 0.03 | 0.01 | 0.04 |
| Sulfate (mg/l) | 9.73 | 39.26 | 16.52 | 58.42 | 16.21 | 41.16 |
| Fluoride (mg/l) | 0.036 | 0.621 | 0.166 | 0.768 | 0.072 | 0.756 |
| Chloride (mg/l) | 40 | 280 | 60 | 225 | 55 | 210 |
| Turbidity (NTU) | 0.001 | 0.001 | 0 | 0.001 | 0 | 0.001 |
| Arsenic (mg/l) | BDL | 0.0003 | 0.0004 | 0.0008 | 0.0008 | 0.0007 |
| Copper (mg/l) | 0.0015 | 0.0011 | 0.0012 | 0.0006 | 0.0004 | 0.0008 |
| Cadmium (mg/l) | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.0021 | 0.0038 | 0.0018 | 0.0004 | 0.0013 | 0.0004 |
| Lead (mg/l) | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.1621 | 0.3219 | 0.0955 | 0.1528 | 0.0990 | 0.2360 |
| Zinc (mg/l) | 0.0776 | 0.0236 | 0.0375 | 0.0653 | 0.0331 | 0.0243 |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 |

TABLE 3 – VARIOUS RESIDENTIAL LOCATIONS

| Parameters | T1 (193B) | T2 (203) | T3D (385) | T3F (318) | T4 (4089) | T5 (505) | T6 (644) | Multistory Building-A (101) | Multistory Building-B (103) | Multistory Building-C (104) | Multistory Building-D (102) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 8.26 | 8.23 | 7.95 | 8.39 | 8.41 | 8.34 | 8.37 | 7.89 | 8.15 | 8.19 | 8.23 |
| TDS (mg/l) | 640 | 632 | 392 | 486 | 391 | 597 | 395 | 744 | 722 | 729 | 722 |
| Hardness (as CaCO3) (mg/l) | 140 | 100 | 90 | 130 | 150 | 140 | 120 | 220 | 160 | 160 | 190 |
| Alkalinity (as CaCO3) (mg/l) | 230 | 260 | 310 | 200 | 380 | 240 | 320 | 220 | 210 | 220 | 200 |
| Nitrate (mg/l) | 0.25 | 0.15 | 0.21 | 0.15 | 0.39 | 0.18 | 0.41 | 0.06 | 0.08 | 0.02 | 0.05 |
| Sulfate (mg/l) | 54.78 | 42.10 | 49.24 | 46.36 | 38.25 | 57.54 | 51.57 | 65.21 | 59.54 | 71.51 | 73.78 |
| Fluoride (mg/l) | 0.709 | 0.808 | 0.984 | 0.946 | 0.974 | 0.884 | 0.949 | 0.518 | 0.534 | 0.584 | 0.602 |
| Chloride (mg/l) | 300 | 250 | 95 | 155 | 100 | 210 | 95 | 295 | 305 | 250 | 280 |
| Turbidity (NTU) | 0 | 0.001 | 0.001 | 0.001 | 0.001 | 0 | 0.001 | 0.001 | 0.002 | 0.001 | 0.001 |
| Arsenic (mg/l) | 0.0012 | 0.0002 | 0.0024 | 0.0015 | 0.0023 | 0.0012 | 0.0024 | 0.0009 | 0.0009 | 0.0008 | 0.0010 |
| Copper (mg/l) | 0.0007 | 0.0009 | 0.0010 | 0.0006 | 0.0004 | 0.0003 | 0.0009 | 0.0006 | 0.0009 | 0.0019 | 0.0013 |
| Cadmium (mg/l) | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.0035 | 0.0039 | 0.0046 | 0.0045 | 0.0040 | 0.0044 | 0.0045 | 0.0036 | 0.0039 | 0.0041 | 0.0039 |
| Lead (mg/l) | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.2718 | 0.3004 | 0.1264 | 0.2185 | 0.1254 | 0.2503 | 0.1341 | 0.2204 | 0.2913 | 0.2284 | 0.2439 |
| Zinc (mg/l) | 0.0060 | 0.1189 | 0.0439 | 0.1217 | 0.0743 | 0.0194 | 0.0728 | 0.0573 | 0.0896 | 0.0212 | 0.0543 |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Sampling locations:

Pumps P1 – Opp. Type 2 shop-C  near water tank, P2- End of lane 37 near house 4098, P3 – Behind Helicopter building,

P7 -  Near water tank and main entrance of  VH-Extension , type-1, P-8 Near Health Centre,  P-12 - Near about 150 M of

P-2 (end of lane-36), P13 – Near Visiting Faculty Apartment, P14 Near Hall 12,

Hall 1 to RA2 various hostels; VH- Visitors Hostel; HC- Health Centre;

T1 to T6 Residences with corresponding House Numbers.

Multistory Building A to D- New faculty buildings with corresponding House Numbers.

- BDL Below Detection Limit; NTU – Nephelometric Turbidity Unit; cfu - Colony forming Units in 100 ml of the sample

- Detection Limits Pb 0.0001 mg/l, Cu 0.0001 mg/l , Cr 0.0005mg/l ,Fe 0.0001 mg/l , Cd 0.0004 mg/l,  As 0.0001 mg/l,  Zn 0.0005 mg/l