RESULTS OF THE WATER QUALITY PARAMETERS OF the institute

(SAMPLING DATE 24/02/22)

| Parameters | Permissible Limit | Maximum Limit | P3 | P11 | P12 | P13 | P14 | P15 | P16 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 6.5 to 8.5 | No relaxation | 7.45 | 7.39 | 7.87 | 7.94 | 7.76 | 7.51 | 7.86 |
| TDS (mg/l) | 500 | 2000 | 436 | 660 | 393 | 560 | 651 | 701 | 399 |
| Hardness (as CaCO3) (mg/l) | 200 | 600 | 140 | 150 | 160 | 120 | 140 | 130 | 160 |
| Alkalinity(as CaCO3) (mg/l) | 200 | 600 | 360 | 280 | 350 | 320 | 280 | 310 | 340 |
| Nitrate (mg/l) | 45 | No relaxation | 0.14 | 0.08 | 0.06 | 0.11 | 0.09 | 0.07 | 0.06 |
| Sulfate (mg/l) | 200 | 400 | 28.57 | 41.68 | 26.94 | 43.36 | 49.78 | 43.26 | 25.84 |
| Fluoride (mg/l) | 1 | 1.5 | 0.786 | 0.632 | 0.842 | 0.728 | 0.562 | 0.586 | 0.792 |
| Chloride (mg/l) | 250 | 1000 | 130 | 275 | 90 | 200 | 285 | 215 | 100 |
| Turbidity (NTU) | 5 | 10 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Arsenic (mg/l) | 0.01 | 0.05 | 0.0021 | 0.0025 | 0.0031 | 0.0029 | 0.0027 | 0.0024 | 0.0028 |
| Copper (mg/l) | 0.05 | 1.5 | 0.0031 | 0.0024 | 0.0017 | 0.0024 | 0.0026 | 0.0033 | 0.0021 |
| Cadmium (mg/l) | 0.003 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.05 | No relaxation | 0.0017 | 0.0016 | 0.0021 | 0.0019 | 0.0020 | 0.0016 | 0.0014 |
| Lead (mg/l) | 0.01 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.3 | No relaxation | 0.16 | 0.18 | 0.21 | 0.12 | 0.15 | 0.17 | 0.14 |
| Zinc (mg/l) | 5 | 15 | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Sampling Locations: P3 – Behind Helicopter building, P-11 Hall 10 back side,  P-12 - Near about 150 M of P-2 (end of lane-36), P13 – Near Visiting Faculty Apartment, P14 Near Hall 12, P15 Behind New Sac, P19 – Near duplex type-3

BDL Below Detection Limit;  NTU – Nephelometric Turbidity Unit; cfu-  Colony forming Units in 100 ml of the sample

Detection Limits Pb 0.0001 mg/l, Cu 0.0001 mg/l , Cr 0.0005 mg/l ,Fe 0.0001 mg/l , Cd 0.0004 mg/l, As 0.0001 mg/l, Zn 0.0005 mg/l