RESULTS OF THE WATER QUALITY PARAMETERS OF the institute

(SAMPLING DATE 29/01/20)

| Parameters | Permissible Limit | Maximum Limit | P1 | P2 | P3 | P7 | P8 | P12 | P13 | P14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 6.5 to 8.5 | No relaxation | 8.02 | 8.19 | 8.29 | 7.98 | 8.21 | 8.42 | 8.38 | 8.32 |
| TDS (mg/l) | 500 | 2000 | 472 | 532 | 457 | 658 | 774 | 394 | 528 | 640 |
| Hardness (as CaCO3) (mg/l) | 200 | 600 | 90 | 160 | 90 | 100 | 170 | 80 | 110 | 140 |
| Alkalinity(as CaCO3) (mg/l) | 200 | 600 | 290 | 490 | 330 | 260 | 250 | 320 | 260 | 280 |
| Nitrate (mg/l) | 45 | No relaxation | 0.08 | 0.38 | 0.07 | 0.06 | 0.11 | 0.18 | 0.16 | 0.08 |
| Sulfate (mg/l) | 200 | 400 | 28 | 39 | 43 | 45 | 56 | 41 | 37 | 25 |
| Fluoride (mg/l) | 1 | 1.5 | 0.745 | 0.795 | 0.812 | 0.598 | 0.649 | 0.789 | 0.794 | 0.658 |
| Chloride (mg/l) | 250 | 1000 | 160 | 95 | 135 | 275 | 300 | 100 | 220 | 290 |
| Turbidity (NTU) | 5 | 10 | 0.001 | 0.001 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Arsenic (mg/l) | 0.01 | 0.05 | 0.0021 | 0.0008 | 0.0022 | 0.0016 | 0.0014 | 0.0028 | BDL | 0.0008 |
| Copper (mg/l) | 0.05 | 1.5 | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Cadmium (mg/l) | 0.003 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.05 | No relaxation | 0.0032 | 0.0074 | 0.0053 | 0.0040 | 0.0042 | 0.0048 | 0.0033 | 0.0043 |
| Lead (mg/l) | 0.01 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.3 | No relaxation | 0.10 | 0.18 | 0.15 | 0.12 | 0.18 | 0.15 | 0.22 | 0.14 |
| Zinc (mg/l) | 5 | 15 | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Sampling Locations:  P1 – Opp. Type 2 shop-C  near water tank, P2- End of lane 37 near house 4098, P3 – Behind Helicopter building,   P7 -  Near water tank and main entrance of  VH-Extension , type-1, P-8 Near Health Centre,  P-12 - Near about 150 M of  P-2 (end of lane-36), P13 – Near Visiting Faculty Apartment, P14 Near Hall 12,

BDL Below Detection Limit;  NTU – Nephelometric Turbidity Unit; cfu-  Colony forming Units in 100 ml of the sample

Detection Limits Pb 0.0001 mg/l, Cu 0.0001 mg/l , Cr 0.0005 mg/l ,Fe 0.0001 mg/l , Cd 0.0004 mg/l, As 0.0001 mg/l, Zn 0.0005 mg/l