RESULTS OF THE WATER QUALITY PARAMETERS OF the institute

(SAMPLING DATE 23/06/22)

| Parameters | Permissible Limit | Maximum Limit | P3 | P7 | P8 | P11 | P12 | P13 | P14 | P15 | P16 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 6.5 to 8.5 | No relaxation | 7.64 | 7.51 | 7.47 | 7.38 | 7.79 | 7.65 | 7.45 | 7.76 | 7.98 |
| TDS (mg/l) | 500 | 2000 | 445 | 636 | 762 | 664 | 405 | 586 | 645 | 736 | 417 |
| Hardness (as CaCO3) (mg/l) | 200 | 600 | 100 | 160 | 120 | 140 | 100 | 130 | 140 | 160 | 110 |
| Alkalinity (as CaCO3) (mg/l) | 200 | 600 | 350 | 300 | 290 | 280 | 340 | 320 | 280 | 300 | 320 |
| Nitrate (mg/l) | 45 | No relaxation | 0.12 | 0.06 | 0.08 | 0.10 | 0.07 | 0.11 | 0.06 | 0.09 | 0.07 |
| Sulfate (mg/l) | 200 | 400 | 41.05 | 56.06 | 49.61 | 39.42 | 35.15 | 54.21 | 37.78 | 35.57 | 32.84 |
| Fluoride (mg/l) | 1 | 1.5 | 0.833 | 0.621 | 0.578 | 0.643 | 0.844 | 0.713 | 0.584 | 0.594 | 0.798 |
| Chloride (mg/l) | 250 | 1000 | 130 | 270 | 285 | 275 | 90 | 190 | 280 | 310 | 100 |
| Turbidity (NTU) | 5 | 10 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Arsenic (mg/l) | 0.01 | 0.05 | 0.0028 | 0.0031 | 0.0029 | 0.0027 | 0.0036 | 0.0025 | 0.0028 | 0.0023 | 0.0027 |
| Copper (mg/l) | 0.05 | 1.5 | 0.0032 | 0.0026 | 0.0030 | 0.0037 | 0.0039 | 0.0018 | 0.0031 | 0.0036 | 0.0034 |
| Cadmium (mg/l) | 0.003 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.05 | No relaxation | 0.0016 | 0.0019 | 0.0024 | 0.0018 | 0.0021 | 0.0015 | 0.0018 | 0.0013 | 0.0016 |
| Lead (mg/l) | 0.01 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.3 | No relaxation | 0.15 | 0.20 | 0.11 | 0.14 | 0.21 | 0.17 | 0.15 | 0.17 | 0.16 |
| Zinc (mg/l) | 5 | 15 | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Sampling Locations: P3 – Behind Helicopter building, P7 -  Near water tank and main entrance of  VH-Extension , type-1, P-8 Near Health Centre, P-11 Hall 10 back side,  P-12 - Near about 150 M of P-2 (end of lane-36), P13 – Near Visiting Faculty Apartment, P14 Near Hall 12, P15 Behind New Sac, P16  Near duplex type-3

BDL Below Detection Limit;  NTU – Nephelometric Turbidity Unit; cfu-  Colony forming Units in 100 ml of the sample

Detection Limits Pb 0.0001 mg/l, Cu 0.0001 mg/l , Cr 0.0005 mg/l ,Fe 0.0001 mg/l , Cd 0.0004 mg/l, As 0.0001 mg/l, Zn 0.0005 mg/l