RESULTS OF THE WATER QUALITY PARAMETERS OF the institute

(SAMPLING DATE 28/03/22)

| Parameters | Permissible Limit | Maximum Limit | P1 | P3 | P7 | P8 | P11 | P12 | P13 | P14 | P15 | P16 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 6.5 to 8.5 | No relaxation | 7.81 | 7.92 | 7.52 | 7.69 | 7.58 | 8.19 | 7.96 | 7.99 | 8.05 | 8.18 |
| TDS (mg/l) | 500 | 2000 | 579 | 448 | 634 | 784 | 664 | 406 | 562 | 648 | 698 | 407 |
| Hardness (as CaCO3) (mg/l) | 200 | 600 | 110 | 130 | 140 | 130 | 150 | 160 | 130 | 120 | 130 | 150 |
| Alkalinity(as CaCO3) (mg/l) | 200 | 600 | 330 | 360 | 280 | 310 | 300 | 350 | 300 | 260 | 270 | 350 |
| Nitrate (mg/l) | 45 | No relaxation | 0.15 | 0.11 | 0.08 | 0.04 | 0.10 | 0.07 | 0.11 | 0.08 | 0.09 | 0.07 |
| Sulfate (mg/l) | 200 | 400 | 38.59 | 32.45 | 25.93 | 43.75 | 48.25 | 29.14 | 51.28 | 45.32 | 39.86 | 21.97 |
| Fluoride (mg/l) | 1 | 1.5 | 0.741 | 0.762 | 0.553 | 0.496 | 0.578 | 0.753 | 0.641 | 0.514 | 0.508 | 0.753 |
| Chloride (mg/l) | 250 | 1000 | 195 | 130 | 265 | 300 | 280 | 95 | 200 | 280 | 310 | 100 |
| Turbidity (NTU) | 5 | 10 | 0.001 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Arsenic (mg/l) | 0.01 | 0.05 | 0.0027 | 0.0024 | 0.0029 | 0.0032 | 0.0028 | 0.0034 | 0.0026 | 0.0025 | 0.0028 | 0.0027 |
| Copper (mg/l) | 0.05 | 1.5 | 0.0014 | 0.0032 | 0.0031 | 0.0029 | 0.0026 | 0.0019 | 0.0021 | 0.0023 | 0.0036 | 0.0029 |
| Cadmium (mg/l) | 0.003 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.05 | No relaxation | 0.0032 | 0.0015 | 0.0019 | 0.0022 | 0.0017 | 0.0021 | 0.0023 | 0.0019 | 0.0018 | 0.0014 |
| Lead (mg/l) | 0.01 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.3 | No relaxation | 0.19 | 0.15 | 0.17 | 0.12 | 0.14 | 0.21 | 0.14 | 0.16 | 0.17 | 0.15 |
| Zinc (mg/l) | 5 | 15 | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Sampling Locations: P1 – Opp. Type 2 shop-C  near water tank, P3 – Behind Helicopter building, P7 -  Near water tank and main entrance of  VH-Extension , type-1, P-8 Near Health Centre,  P-11 Hall 10 back side,  P-12 - Near about 150 M of P-2 (end of lane-36), P13 Near Visiting Faculty Apartment, P14 Near Hall 12, P15 Behind New Sac, P16  Near duplex type-3

BDL Below Detection Limit;  NTU – Nephelometric Turbidity Unit; cfu-  Colony forming Units in 100 ml of the sample

Detection Limits Pb 0.0001 mg/l, Cu 0.0001 mg/l , Cr 0.0005 mg/l ,Fe 0.0001 mg/l , Cd 0.0004 mg/l, As 0.0001 mg/l, Zn 0.0005 mg/l