RESULTS OF THE WATER QUALITY PARAMETERS OF the institute

(SAMPLING DATE 27/05/20)

| Parameters | Permissible Limit | Maximum Limit | P1 | P2 | P3 | P8 | P11 | P12 | P13 | P14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 6.5 to 8.5 | No relaxation | 7.87 | 7.41 | 8.27 | 8.11 | 8.36 | 8.21 | 8.31 | 8.33 |
| TDS (mg/l) | 500 | 2000 | 490 | 493 | 452 | 771 | 647 | 403 | 570 | 641 |
| Hardness (as CaCO3) (mg/l) | 200 | 600 | 100 | 150 | 90 | 160 | 140 | 80 | 140 | 110 |
| Alkalinity(as CaCO3) (mg/l) | 200 | 600 | 320 | 500 | 310 | 280 | 290 | 310 | 290 | 260 |
| Nitrate (mg/l) | 45 | No relaxation | 0.11 | 0.36 | 0.08 | 0.06 | 0.21 | 0.18 | 0.14 | 0.07 |
| Sulfate (mg/l) | 200 | 400 | 22.01 | 18.68 | 16.73 | 39.89 | 43.57 | 30.42 | 34.21 | 21.15 |
| Fluoride (mg/l) | 1 | 1.5 | 0.780 | 0.942 | 0.819 | 0.519 | 0.720 | 0.791 | 0.757 | 0.598 |
| Chloride (mg/l) | 250 | 1000 | 155 | 85 | 125 | 305 | 280 | 100 | 210 | 275 |
| Turbidity (NTU) | 5 | 10 | 0.001 | 0.001 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Arsenic (mg/l) | 0.01 | 0.05 | 0.0021 | 0.0016 | 0.0026 | 0.0014 | 0.0025 | 0.0028 | 0.0025 | 0.0029 |
| Copper (mg/l) | 0.05 | 1.5 | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Cadmium (mg/l) | 0.003 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.05 | No relaxation | 0.0044 | 0.0075 | 0.0055 | 0.0047 | 0.0034 | 0.0054 | 0.0052 | 0.0046 |
| Lead (mg/l) | 0.01 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.3 | No relaxation | 0.31 | 0.18 | 0.21 | 0.29 | 0.21 | 0.15 | 0.18 | 0.16 |
| Zinc (mg/l) | 5 | 15 | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Sampling Locations:  P1 – Opp. Type 2 shop-C  near water tank, P2- End of lane 37 near house 4098, P3 – Behind Helicopter building,  P-8 Near Health Centre, P-11 Hall 10 back side,  P-12 - Near about 150 M of  P-2 (end of lane-36), P13 – Near Visiting Faculty Apartment, P14 Near Hall 12

BDL Below Detection Limit;  NTU – Nephelometric Turbidity Unit; cfu-  Colony forming Units in 100 ml of the sample

Detection Limits Pb 0.0001 mg/l, Cu 0.0001 mg/l , Cr 0.0005 mg/l ,Fe 0.0001 mg/l , Cd 0.0004 mg/l, As 0.0001 mg/l, Zn 0.0005 mg/l