RESULTS OF THE WATER QUALITY PARAMETERS OF the institute

(SAMPLING DATE 25/11/20)

| Parameters | Permissible Limit | Maximum Limit | P1 | P3 | P7 | P8 | P11 | P12 | P13 | P14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 6.5 to 8.5 | No relaxation | 7.91 | 8.01 | 7.82 | 7.93 | 8.02 | 8.28 | 8.05 | 8.10 |
| TDS (mg/l) | 500 | 2000 | 499 | 447 | 644 | 760 | 640 | 393 | 585 | 653 |
| Hardness (as CaCO3) (mg/l) | 200 | 600 | 100 | 110 | 130 | 140 | 150 | 100 | 120 | 110 |
| Alkalinity(as CaCO3) (mg/l) | 200 | 600 | 330 | 310 | 270 | 230 | 280 | 320 | 270 | 230 |
| Nitrate (mg/l) | 45 | No relaxation | 0.14 | 0.06 | 0.07 | 0.04 | 0.16 | 0.11 | 0.08 | 0.10 |
| Sulfate (mg/l) | 200 | 400 | 35.94 | 31.05 | 39.26 | 48.42 | 41.84 | 33.47 | 41.57 | 49.72 |
| Fluoride (mg/l) | 1 | 1.5 | 0.698 | 0.817 | 0.581 | 0.621 | 0.624 | 0.824 | 0.692 | 0.697 |
| Chloride (mg/l) | 250 | 1000 | 165 | 120 | 275 | 300 | 260 | 95 | 210 | 275 |
| Turbidity (NTU) | 5 | 10 | 0.001 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Arsenic (mg/l) | 0.01 | 0.05 | 0.0023 | 0.0027 | 0.0027 | 0.0029 | 0.0028 | 0.0033 | 0.0028 | 0.0029 |
| Copper (mg/l) | 0.05 | 1.5 | 0.0016 | 0.0014 | 0.0021 | 0.0026 | 0.0096 | 0.0023 | 0.0023 | 0.0029 |
| Cadmium (mg/l) | 0.003 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.05 | No relaxation | 0.0016 | 0.0015 | 0.0018 | 0.0015 | 0.0026 | 0.0018 | 0.0018 | 0.0016 |
| Lead (mg/l) | 0.01 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.3 | No relaxation | 0.26 | 0.12 | 0.14 | 0.11 | 0.18 | 0.19 | 0.10 | 0.14 |
| Zinc (mg/l) | 5 | 15 | 0.0048 | 0.0012 | 0.0025 | BDL | 0.0062 | 0.0039 | 0.0030 | 0.0029 |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Sampling Locations:  P1 – Opp. Type 2 shop-C  near water tank, P3 – Behind Helicopter building, P7 -  Near water tank and main entrance of  VH-Extension , type-1, P-8 Near Health Centre, P-11 Hall 10 back side,  P-12 - Near about 150 M of  P-2 (end of lane-36), P13 – Near Visiting Faculty Apartment, P14 Near Hall 12,

BDL Below Detection Limit;  NTU – Nephelometric Turbidity Unit; cfu-  Colony forming Units in 100 ml of the sample

Detection Limits Pb 0.0001 mg/l, Cu 0.0001 mg/l , Cr 0.0005 mg/l ,Fe 0.0001 mg/l , Cd 0.0004 mg/l, As 0.0001 mg/l, Zn 0.0005 mg/l