RESULTS OF THE WATER QUALITY PARAMETERS OF the institute

(SAMPLING DATE 20/10/20)

| Parameters | Permissible Limit | Maximum Limit | P1 | P2 | P3 | P8 | P11 | P12 | P13 | P14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 6.5 to 8.5 | No relaxation | 8.14 | 8.41 | 8.49 | 8.32 | 8.37 | 8.47 | 8.17 | 8.27 |
| TDS (mg/l) | 500 | 2000 | 496 | 354 | 436 | 774 | 633 | 383 | 577 | 642 |
| Hardness (as CaCO3) (mg/l) | 200 | 600 | 100 | 120 | 110 | 130 | 140 | 100 | 120 | 110 |
| Alkalinity(as CaCO3) (mg/l) | 200 | 600 | 310 | 400 | 300 | 250 | 330 | 300 | 290 | 260 |
| Nitrate (mg/l) | 45 | No relaxation | 0.18 | 0.21 | 0.07 | 0.06 | 0.17 | 0.11 | 0.10 | 0.06 |
| Sulfate (mg/l) | 200 | 400 | 25.02 | 16.52 | 19.62 | 32.41 | 28.72 | 35.81 | 45.32 | 31.71 |
| Fluoride (mg/l) | 1 | 1.5 | 0.756 | 0.823 | 0.768 | 0.648 | 0.722 | 0.778 | 0.829 | 0.742 |
| Chloride (mg/l) | 250 | 1000 | 160 | 45 | 125 | 300 | 270 | 100 | 215 | 275 |
| Turbidity (NTU) | 5 | 10 | 0.001 | 0.001 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Arsenic (mg/l) | 0.01 | 0.05 | 0.0024 | 0.0015 | 0.0027 | 0.0029 | 0.0027 | 0.0034 | 0.0027 | 0.0030 |
| Copper (mg/l) | 0.05 | 1.5 | 0.0037 | 0.0016 | 0.0023 | 0.0035 | 0.0031 | 0.0023 | 0.0030 | 0.0033 |
| Cadmium (mg/l) | 0.003 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.05 | No relaxation | 0.0035 | 0.0024 | 0.0018 | 0.0012 | 0.0032 | 0.0016 | 0.0015 | 0.0016 |
| Lead (mg/l) | 0.01 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.3 | No relaxation | 0.24 | 0.21 | 0.14 | 0.11 | 0.16 | 0.18 | 0.10 | 0.12 |
| Zinc (mg/l) | 5 | 15 | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Sampling Locations:  P1 – Opp. Type 2 shop-C  near water tank, P2- End of lane 37 near house 4098, P3 – Behind Helicopter building, P-8 Near Health Centre, P-11 Hall 10 back side,  P-12 - Near about 150 M of  P-2 (end of lane-36), P13 – Near Visiting Faculty Apartment, P14 Near Hall 12,

BDL Below Detection Limit;   NTU – Nephelometric Turbidity Unit; cfu-  Colony forming Units in 100 ml of the sample

Detection Limits Pb 0.0001 mg/l, Cu 0.0001 mg/l , Cr 0.0005 mg/l ,Fe 0.0001 mg/l , Cd 0.0004 mg/l, As 0.0001 mg/l, Zn 0.0005 mg/l