RESULTS OF THE WATER QUALITY PARAMETERS OF the institute

(SAMPLING DATE 28/10/21)

| Parameters | Permissible Limit | Maximum Limit | P3 | P7 | P8 | P11 | P12 | P13 | P14 | P15 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 6.5 to 8.5 | No relaxation | 8.14 | 8.21 | 7.95 | 8.11 | 8.25 | 8.32 | 7.84 | 7.89 |
| TDS (mg/l) | 500 | 2000 | 448 | 634 | 786 | 673 | 412 | 581 | 665 | 692 |
| Hardness (as CaCO3) (mg/l) | 200 | 600 | 110 | 150 | 120 | 150 | 100 | 160 | 160 | 130 |
| Alkalinity(as CaCO3) (mg/l) | 200 | 600 | 320 | 280 | 270 | 260 | 320 | 290 | 260 | 270 |
| Nitrate (mg/l) | 45 | No relaxation | 0.09 | 0.05 | 0.07 | 0.12 | 0.14 | 0.06 | 0.10 | 0.09 |
| Sulfate (mg/l) | 200 | 400 | 28.18 | 32.48 | 45.64 | 33.52 | 30.84 | 45.53 | 28.92 | 41.83 |
| Fluoride (mg/l) | 1 | 1.5 | 0.792 | 0.586 | 0.562 | 0.641 | 0.812 | 0.697 | 0.632 | 0.678 |
| Chloride (mg/l) | 250 | 1000 | 130 | 310 | 295 | 300 | 180 | 120 | 250 | 235 |
| Turbidity (NTU) | 5 | 10 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Arsenic (mg/l) | 0.01 | 0.05 | 0.0027 | 0.0025 | 0.0032 | 0.0026 | 0.0038 | 0.0028 | 0.0029 | 0.0026 |
| Copper (mg/l) | 0.05 | 1.5 | 0.0023 | 0.0037 | 0.0021 | 0.0027 | 0.0017 | 0.0025 | 0.0020 | 0.0026 |
| Cadmium (mg/l) | 0.003 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.05 | No relaxation | 0.0016 | 0.0021 | 0.0018 | 0.0017 | 0.0017 | 0.0014 | 0.0016 | 0.0018 |
| Lead (mg/l) | 0.01 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.3 | No relaxation | 0.19 | 0.11 | 0.12 | 0.14 | 0.19 | 0.13 | 0.15 | 0.16 |
| Zinc (mg/l) | 5 | 15 | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Sampling Locations:   P3 – Behind Helicopter building, P7 -  Near water tank and main entrance of  VH-Extension , type-1, P-8 Near Health Centre, P-11 Hall 10 back side,  P-12 - Near about 150 M of  P-2 (end of lane-36), P13 – Near Visiting Faculty Apartment, P14 Near Hall 12, P15 Near New SAC

BDL Below Detection Limit;  NTU – Nephelometric Turbidity Unit; cfu-  Colony forming Units in 100 ml of the sample

Detection Limits Pb 0.0001 mg/l, Cu 0.0001 mg/l , Cr 0.0005 mg/l ,Fe 0.0001 mg/l , Cd 0.0004 mg/l, As 0.0001 mg/l, Zn 0.0005 mg/l