RESULTS OF THE WATER QUALITY PARAMETERS OF the institute

(SAMPLING DATE 30/07/20)

| Parameters | Permissible Limit | Maximum Limit | P1 | P2 | P3 | P7 | P8 | P11 | P12 | P13 | P14 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| pH | 6.5 to 8.5 | No relaxation | 7.73 | 7.64 | 7.79 | 7.71 | 7.92 | 7.71 | 7.91 | 7.73 | 7.80 |
| TDS (mg/l) | 500 | 2000 | 583 | 765 | 448 | 655 | 391 | 657 | 391 | 644 | 500 |
| Hardness (as CaCO3) (mg/l) | 200 | 600 | 150 | 160 | 110 | 120 | 80 | 130 | 90 | 120 | 100 |
| Alkalinity(as CaCO3) (mg/l) | 200 | 600 | 300 | 310 | 360 | 280 | 320 | 290 | 320 | 280 | 340 |
| Nitrate (mg/l) | 45 | No relaxation | 0.12 | 0.22 | 0.07 | 0.06 | 0.09 | 0.24 | 0.16 | 0.11 | 0.08 |
| Sulfate (mg/l) | 200 | 400 | 24.05 | 15.54 | 20.14 | 35.92 | 32.65 | 41.21 | 28.35 | 38.54 | 18.24 |
| Fluoride (mg/l) | 1 | 1.5 | 0.774 | 0.624 | 0.878 | 0.680 | 0.972 | 0.818 | 0.970 | 0.659 | 0.928 |
| Chloride (mg/l) | 250 | 1000 | 250 | 100 | 135 | 270 | 320 | 295 | 100 | 275 | 185 |
| Turbidity (NTU) | 5 | 10 | 0.001 | 0.001 | 0.002 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Arsenic (mg/l) | 0.01 | 0.05 | 0.0025 | 0.0028 | 0.0027 | 0.0027 | 0.0031 | 0.0028 | 0.0032 | 0.0029 | 0.0026 |
| Copper (mg/l) | 0.05 | 1.5 | 0.0025 | 0.0029 | 0.0024 | 0.0036 | 0.0027 | 0.0035 | 0.0029 | 0.0030 | 0.0029 |
| Cadmium (mg/l) | 0.003 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Chromium (mg/l) | 0.05 | No relaxation | 0.0008 | 0.0013 | 0.0009 | 0.0015 | 0.0043 | 0.0020 | 0.0012 | 0.0010 | 0.0018 |
| Lead (mg/l) | 0.01 | No relaxation | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Iron (mg/l) | 0.3 | No relaxation | 0.29 | 0.21 | 0.16 | 0.18 | 0.25 | 0.17 | 0.18 | 0.21 | 0.18 |
| Zinc (mg/l) | 5 | 15 | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL | BDL |
| Fecal Coliform (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |
| E. Coli (cfu) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |

Sampling Locations:  P1 – Opp. Type 2 shop-C  near water tank, P2- End of lane 37 near house 4098,

P3 – Behind Helicopter building, P7 -  Near water tank and main entrance of  VH-Extension , type-1,

P-8 Near Health Centre, P-11 Hall 10 back side,  P-12 - Near about 150 M of  P-2 (end of lane-36),

P13 – Near Visiting Faculty Apartment, P14 Near Hall 12

BDL Below Detection Limit;  NTU – Nephelometric Turbidity Unit; cfu-  Colony forming Units in 100 ml of the sample

Detection Limits Pb 0.0001 mg/l, Cu 0.0001 mg/l , Cr 0.0005 mg/l ,Fe 0.0001 mg/l , Cd 0.0004 mg/l, As 0.0001 mg/l, Zn 0.0005 mg/l